## MG COVER PAGE
Name of Distribution Licensee: M G V C L
Quarter : Q-I I (July-Aug-Sept- 2021)
Year: 2021-22

## SOP 01
Name of Distribution Licensee: M G V C L
Quarter:2 (JUL -Aug- SEP-21)
Year:2021-22
Performa - SoP 001: Fatal and Non-Fatal electrical accident report
NUMBER OF ACCIDENTS FOR THE 2nd QUARTER OF 2021-22
Sr.No | Name of Area/Circle | No of accidents in 2nd quarter |  |  |  |  | Cumulative since the first quarter of the current FY 2021-22
|  | Departmental |  | Outsider |  |  | TOTAL
|  | FH | NFH | FH | FA | NFH | FH | FA | NFH
1 | Baroda (O&M) | 0 | 1 | 1 | 1 | 0 | 1 | 4 | 1
2 | Baroda City | 0 | 1 | 1 | 11 | 1 | 3 | 20 | 4
3 | Anand | 0 | 0 | 2 | 2 | 0 | 6 | 9 | 0
4 | Nadiad | 1 | 1 | 2 | 12 | 2 | 6 | 29 | 3
5 | Godhra | 0 | 0 | 1 | 4 | 0 | 4 | 13 | 2
| TOTAL | 1 | 3 | 7 | 30 | 3 | 20 | 75 | 10
FH – Fatal Human, FA – Fatal Animal, NFH – Non-fatal Human
PVT - Private Premises Accident.

## SOP02
Performa – SoP 003: Action taken report for safety measures complied for the accidents occurred
ACTION TAKEN REPORT FOR SAFETY MEASURES COMPLIED FOR THE ACCIDENTS OCCURED IN THE 2nd QUARTER OF FY2021-22
Sr. No | Location of Accident and details of the victim | Address | sdn | Date of occurrence | Type of Accident | Installation | Accident Type | Cause of Accident | Findings of CEI / EI / AEI | Remedies suggested by CEI /EI / AEI in various cases | Whether the remedy suggested is complied | Action taken to avoid recurrence of such Accident |  |  | Circle office | Reasons
1 | MANGTABHAI JIVABHAI NOKAM (LM), Behind S/S, Vill-Kathla, Tal/Dist-Dahod |  |  | 2021-07-06 | FHD |  |  | The victim was trying to remove dead 11KV span between 11KV KATWARA JGY AND 11KV RACHHARDA JGY feeder emanating from 66KV KATHLA S/S. Shri C M Parmar climbed on 11kv Rachharda JGY feeder (LC ALREADY TAKEN) and victim climbed on 11kv Katwara JGY feeder (LC NOT TAKEN).While removing the middle conductor of dead span, victim came in contact with live 11kv conductor of Katwara JGY feeder and got electrocuted which resulted into fatal electrical accident. | Awaited | NA | NA | LINE STAFF IS STRICTLY INSTRUCTED IN SAFETY MEETING TO CHECK AND CONFIRM WHETHER POWER SUPPLY IS MADE OFF OR NOT BEFORE CLIMBING ON POLE. | No | 2508/07.07.2021 | Godhra | 2
2 | NARESHBHAI BACHUBHAI PATEL (ALM), HT CONNECTION M/S INOX LEISURE LTD, Gotri, Vadodara |  |  | 2021-07-09 | NFHD |  |  | During investigation, it was found that during plan shutdown of 11KV Vahanvati feeder he was alloted work of maintenance, while checking jumpers of HT connection CTPT he touched jumpers and got electrocuted. | Awaited | NA | NA | RMU WIRING CHANGED | No | 6033/ 10.07.21 | Baroda City | 3
3 | Owner of Cow shri Narvatbhai Rayjibhai Rathod, vanzar vas, Vill-Delol, Tal-Kalol, Dist-Panchmahal |  |  | 2021-07-10 | FA |  |  | 11KV conductor of delol ag feeder dropped from pin binding and touched with v-cross arm angle due to that leakage current pass through GI earth wire which was contact with v cross angle. The cow came in contact with GI wire and died due to electric shock. | Awaited | NA | NA | Maintenance of line is carried out | No | KSD/T/2412 DTD14.07.2021 | Godhra | 2
4 | Ku.Hiralben Rumalbhai Minama, Vill-Kalakhunt, Tal-Dhanpur, Dist-Dahod |  |  | 2021-07-12 | NFHO |  |  | During primary investigation on spot it has to come that victim was wondering near HT shackle pole of 11kv Mandor JGy FDR and she might be come in contact with PSc pole and get electric shock. | Awaited | NA | NA | Maintenance of line is carried out | NO | GRB/DBD/TECH/ACC/2733 DATE 22.07.2021 | Godhra | 2
5 | SHE BUFFALOW OF SHRI SHANTIBHAI BHAIJIBHAI, HARIJANVAS, Vill-Dhamod, Tal-Lunawada, Dist-Mahisagar |  |  | 2021-07-14 | FA |  |  | A SHE BUFFALOW OF SHRI HANTIBHAI BHAIJIBHAI HARIJAN WAS TIED UNDER VADA NEAR 11KV HT POLE LALSAR AG FEEDER. A BIRD FAULT MIGHT HAVE OCCURED ON SAID 11KV HT POLE AND LEAKAGE CUREENT MAY FALOWN THROUGH THE GI WIRE OF THE POLE AND DURING THIS FAULT THE ANIMAL MAY CAME IN CONTACT WITH GI WIRE AND ELECTROCUTED. | Awaited | NA | NA | NECESSORY MAINTENANCE CARRIED OUT AND POLE EARTHING REACTIVATED | No | (1)KOTHAMBA/1852/14.07.2021 (2)KOTHAMBA/2249/09.08.2021 (3) | Godhra | 2
6 | BUFFALO OWNER: DILIPBHAI MALABHAI RATHOD, KRUSHANAGAR Vill-ANTROLI, Tal-Kapadvanj, Dist-Kheda |  |  | 2021-07-18 | FA |  |  | The top wire of 3Ph 4W LT line slipped from binding and came in contact with U clamp. The leakage current flow from U clamp to GI wire of pole earthing. The buffalo came in contact with GI wire and electrocuted and died. | Awaited | NA | NA | LT line Maintenance was carried out by the sdn. | No | MHD/T/7773/23.07.21 | Nadiad | 2
7 | BUFFALO OF TADVI RAJUBHAI GORDHANBHAI, DHARAMPURI BUS STAND, Vill-Dharampuri, Tal-Dahoi, Dist-Vadodara |  |  | 2021-07-18 | FA |  |  | On date 18.05.2021 at around 11.30 hrs, buffalo carving at Dharampuri Bus stand of Tadvi Rajubhai Gordhanbhai. Due to heavy wind & rain around 11.40 am buffalo accidently touching aluminum stay wire of LT RSJ pole and buffalo got electrocuted and died. | Awaited | NA | NA | REPLACE THE LT GUY WIRE | No | 19.07.21 | Baroda O&M | 2
8 | SHE-BUFFALO, OWNER NAME-PARMAR MAHENDRASINH GANPATSINH, MOTI VARNOLI ROAD, Vill-MOTI VARNOLI, Tal-Desar, Dist-Vadodara |  |  | 2021-07-22 | FA |  |  | She Buffalo grazing near PSC pole. Its leg stuck between Pole and PVC pipe and accidently touch GI wire and got electric shock as AB cable has damaged insulation and touching GI wire. | Awaited | NA | NA | REPLACED BY DAMAGED AB CABLE | No | 24.07.21 | Baroda O&M | 2
9 | Bullock of Somabhai Tadvi, Jambudi Faliya, Vill-Dholpur, Tal-Bodeli, Dist-Chhotaudepur |  |  | 2021-07-25 | FA |  |  | Due to heavy wind and rain on date 25.07.21, in early morning LT open conductor ilne of 2 wire line is short together and phase conductor accidently fall on land. Same time bullok of soma bhai tadvi was tied exact below LT line which electrucuted and died | Awaited | NA | NA | RESTRING OF LOOSE CONDUCTOR | No | 26.07.21 | Baroda O&M | 1
10 | Buffalo owner Chamar Naranbhai Dalabhai, Khanda Faliya (Behind Nagneshwari Temple), Vill-Demli, Tal-Shahera, Dist-Panchmahal |  |  | 2021-07-25 | FA |  |  | The Buffalo was grazing and reached between two poles of TCDP and electrocuted due to leakage current. However at the time of site visit no leakage current noticed. | Awaited | NA | NA | No action required | No | SHR/Tech/5418 DT: 31.07.2021 | Godhra | 2
11 | Buffalo owner Bariya Sandipsinh Hatisinh, Morva (Bhurkhal Three Roads), Vill-Morva, Tal-Shahera, Dist-Panchmahal |  |  | 2021-07-25 | FA |  |  | LT conductor snapped on the Buffalo which was tied below LT line. Buffalo died. | Awaited | NA | NA | Re-stringing & Replacement of LT conductor carried out | No | SHR/Tech/5417 DT: 31.07.2021 | Godhra | 1
12 | Kishanbhai Meena, Umabhavan, Anand |  |  | 2021-07-26 | FHO |  |  | A truck carrying power transformer job may came in contact with 11 kv live wire or Due to Induction and Victim tried to get out of the truck and got electrocuted when his leg came in contact with ground and resulted in to fatal electrical accident | Take action as per CEA Reg-2010 clause no-58 | Take action as per CEA Reg-2010 clause no-58 | Yes | HT line clearance from ground maintained as per CEA Regu 2010 clause no-58 | Yes |  | Anand | 6
13 | BULLOCK, OWNER- DAMOR SABUBHAI MALUBHAI, MEDA FLY, Vill-AAMBALI, Tal-Garbada, Dist-Dahod |  |  | 2021-07-27 | FA |  |  | The bullock may be come in contact with transformer center psc pole or earthing wire and may get electiic shock due to leakage current in neutral earthing wire of transformer center. | Awaited | NA | NA | Transformer earthing reactivated | No | 2800/28.07.2021 | Godhra | 2
14 | Saistaben Hakimbhai Shekh, Khadi Faliya, Nr Husaaini Masjid, Godhra |  |  | 2021-07-28 | NFHO |  |  | AT SITE AS PER THE SITE VISIT THE VICTIM WAS PRESENT NEAR THE PARAFEET WALL OF THE TARRECE AND WHEN VICTIM WAS TRIED TO TAKE MOIST CLOTH UNNECESSORILY THE WATER PIPE OF GI MOVE WHICH WAS PLACED WITH SUPPORT OF NEAREST WALL AND FALLEN ON LIVE 11 KV CONDUCT | Awaited | NA | NA | No action required | No | GDE/TECH/1952 DT: 30.07.2021 | Godhra | 6
15 | HIRAL S. PATEL (EA), ABR/JGY/26/69, IN FARM AT THE ROAD TOWARDS BHRAHMANVASHI VILLAGE, Tal-Padra, Dist-Vadodara |  |  | 2021-07-31 | NFHD |  |  | VICTIM HAD ISOLATED AND CUT OFF OF BOTH 11 KV ABHOR JGY AND MASAR AG THROUGH AB SWITCHES GOING TOWARDS BRAHAMANVASHI VILLAGE, AND THE SUPPLY OF BOTH FEEDER WERE CUT OFF. HE WAS DOING REJUMPERING WORK IN ABHOR JGY, AND SUDDENLY ELECTRIC POWER FELT , HE GOT SHOCK AND FELL DOWN. | Awaited | NA | NA | IMPARTED SAFETY RELATED KNOWLEDGE | No |  | Baroda O&M | 3
16 | Taukir Mosin Pathan, On the boundary of Farm of Shri. Mohanbhai Jethabhai Odd’s Farm and compound of Faiz Residency Vill. Karjan, Tal-Karjan, Dist-Vadodara |  |  | 2021-07-31 | NFHO |  |  | Victim was playing alongwith other kids in the open compound of Faiz Residency.He climbed up on the tree in the neighbouring Mukeshbhai Jethabhai Odd’s farm while playing.While stepping down on the compound wall from the tree,victim lost his balance and touched the conductor of 11KV Anastu Ag feeder and met with accident. | Awaited | NA | NA | VICTIM'S FAULT | No | 02.08.21 | Baroda O&M | 2
17 | BUFFALO owner Chimanbhai Salubhai Rathwa, PATIYA RANGBHUN ROAD, Vill-Patiya, Tal-Jetpur, Dist-Chhotaudepur |  |  | 2021-07-31 | FA |  |  | ACCIDENTALLY FELL IN EARTH PIT UNDER THE TC DP STRUCTURE AND THE BUFFALO CAME IN CONTACT WITH THE EARTH WIRE AND GOT ELECTROCUTED. | Awaited | NA | NA | REACTIVATE EARTHING OF TC | No | 01.08.21 | Baroda O&M | 2
18 | sangada sanjaybhai kadkiyabhai, magnum netlink pvt ltd, Vill-Paldi, Ta-Waghodia, Dist-Vadodara |  |  | 2021-07-13 | FHO |  |  | As per the jarod police station letter received on dtd 17.08.2021 regarding human fatal accident on dtd. 13.07.2021 at location newly construction site magnum netlink pvt ltd near itm college village paldi, and as Per Eye witness statement, Victim (Shri Sanjaybhai Kadkiyabhai Sangada )was doing plastering work of unauthorized New constructed compound wall under 11 kv HT Line and came in contact with the live wire and got electrocuted and met with Fatal accident. | Awaited | NA | NA | NOTICE ISSUED TO MAGNUM NETLINK PVT LTD FOR PROCESS OF LINE SHIFTING | NO | HAT/TECH/NO:2795 DTD 18.08.2021 | Godhra | 6
19 | Bufflow of Patel Hasmukhbhai Mohanbhai, Nr.Bhuri Talavadi,Vill;Waghodia, Ta-Waghodia, Dist-Vadodara |  |  | 2021-08-01 | FA |  |  | While Patel Hasmukhbhai Mohanbhai grazing their buffalos,one of His She buffalo electrocuted due to HT Main Line Y-phase Conductor of 11kv Vyara Ag feeder Broken | Awaited | NA | NA | REBINDING OF CONDUCTOR | No | 04.08.21 | Baroda O&M | 1
20 | She buffalo of shri VASAVA JAGADISHBHAI DHANAJIBHAI, FARM OF PATEL HASAMUKHBHAI CHHITABHAI (KANTESHWER), HARIKUVA PETA PARA OF KANTESHWER, Ta-Sankheda, Dist-Chhotaudepur |  |  | 2021-08-03 | FA |  |  | She buffalo of shri VASAVA JAGADISHBHAI DHANAJIBHAI has rubbed horns on stay wire due to that the stay wire was rusted and broken from anchor rod and touch with LT LINE OF Rustampura AG and hence current was passing to stay wire and buffalow got electrocuted. | Awaited | NA | NA | NEW STAY & STAY WIRE PROVIDED | No | 05.08.21 | Baroda O&M | 2
21 | SHRI YUVRAJSINH JAYSINH TANTOD, Agri Farm of Shri Arvindbhai Punjabhai Valand, Vill-Dodka, Ta/Dist-Vadodara |  |  | 2021-08-14 | FHO |  |  | Victim Shri Yuvrajsinh J.Tantod was working in the farm of A.P.VANAND FOR STRINGING OF THIN G.I WIRE FOR ZATKA MACHINE.SUDDENLY WHEN GOING TO PASS THE THIN G.I .WIRE WITH HOLE OF PSC POLE,LEAKAGE CURRENT PASSED THROUGH LT ABC as INSULATION was DETERIORATED. So leakage current passed through Earth GI wire. The victim came in contact with that and died. | Awaited | NA | NA | VICTIM'S FAULT | No | 16.08.21 | Baroda O&M | 6
22 | Shri Mafatbhai Lakhabhai Rathod, HIORAPURA VISTAR, Vill-Maghrol, Ta-Sojitra, Dist-Anand |  |  | 2021-08-19 | FHO |  |  | 2 wire LT ABC line of 11 kv Dabhou JGY, Maghrol Village TC no. 35. Is passing through psc pole , due to rain Neem Tree Branch fallen on ABC Wire due to that, LT Ab cable snap from LT Sackle and touch to U-Clamp. The insulation of 2W ABC was damaged. So leakage current passed through Earth GI wire. The victim came in contact with that and died. | Awaited | NA | NA | Tree branch was cut and LT ABC Wire was replaced and binding with LT Shackle insulator. | No | SJT/TECH/ACCIDENT/3273 dtd. 23.09.2021 | Anand | 2
23 | PARMAR ALPESHBHAI SOMABHAI, Gandhi faliyu, Vill-Malawada, Ta-Matar, Dist-Kheda |  |  | 2021-08-19 | FHO |  |  | Due to construction of home victim shifted his meter illegally with outsider to adjoining home, Hence SL length increased, so SL stretched & break due to touch with old metal roof and hence leackege current in roof and victim climb for work and got electric shock | Awaited | NA | NA | Service line is replaced by SDO and maintenance is carried out. | No | MHD/T/9333/02.09.2021 & MHD/T/10194/29.09.2021 | Nadiad | 6
24 | PRAVIN RAMESHBHAI SHARMA, A/4/17,SIDDHARTH NAGAR SOCIETY, Vadodara |  |  | 2021-08-20 | FHO |  |  | Victim was climbing on terrace of house no-A/4/17 for fixing /installation of solar panel supporting angle with house terrace perafit wall.Due to unauthorised construction /extension done by the house owner in front side,safety clearance as per norms from | Awaited | NA | NA | NOTICE ISSUED FOR ILLEGAL EXT NEAR HT LINE | No | 7790/ 25.08.21 | Baroda City | 6
25 | BHARVAD BHARATBHAI LAKSHMANBHAI, Vill-BHADRVA, Ta-Savli, Dist-Vadodara |  |  | 2021-08-21 | FA |  |  | street light conductor is layed over our lt pole of JGY rania fdr.Leakage current passed through pole in to the accumulated water near pole from broken insulation of street light conductor | Awaited | NA | NA | NEW POLE erected | No | 23.08.21 | Baroda O&M | 2
26 | Camel of Sureshbhai Varjangbhai Bharvad, KABRASTHAN, Vill-THAMNA, Ta-Umreth, Dist-Anand |  |  | 2021-08-23 | FA |  |  | while eating grass and tree leaves, camel suddenly came in contact with 11 kv thamna ag feeder near the said tree and got electrocuted | Awaited | NA | NA | Proposed TS For Erection of PSC and RSJ Pole for Maintaing HT Line and Ground Clearance | No | 2760/31.8.21 | Anand | 2
27 | Buffalo Owner: Ajitsinh Mansinh Parmar, Sargi New Vasahat, Ta-Bodeli, Dist-Chhotaudepur |  |  | 2021-08-25 | FA |  |  | While buffalo of owner Ajitsinh was roaming around DODP of village TC navi nagari, sargai, it is itching vigorously at stay wire of DODP, hence stay wire broken and touched with outgoing jumper of DODP and get electrucuted. | Awaited | NA | NA | NEW STAY & STAY WIRE PROVIDED | No | 27.08.21 | Baroda O&M | 2
28 | COW of SHANKARBHAI BHAIJIBHAI TADVI, SHANABHAI NATHABHAI PATEL FARM, Vill-Bhatpur, Ta-Sankheda, Dist-Chhotaudepur |  |  | 2021-08-29 | FA |  |  | ON DATED 29.8.2021, AROUND 12:30 PM, COW OF OWNER SHREE SHANKARBHAI BHAIJIBHAI TADVI ROAMING IN FARM OF SHANABHAI NATHABHAI PATEL. AT THAT TIME LT LINE WIRE WAS BROKEN IN FARM DUE TO MONKEY FAULT, DUE TO THIS RESPECTED COW GET IN CONTACT WITH THIS BROKEN LINE AND ELOCTROCUTED | Awaited | NA | NA | REBINDING OF CONDUCTOR | No | 31.08.21 | Baroda O&M | 1
29 | Buffalo OWNER : VAJESING BALSING RATHWA, PANIYA ROAD, PANIYA FALIYU KANJARI, Ta-Halol, Dist-Panchmahal |  |  | 2021-08-31 | FA |  |  | AS PER SITE VISIT IT MAY BE POSSIBLE THAT BUFFALO CAME IN CONTACT WITH LT CONDUCTOR AND GET SHOCKED AND DIED | Awaited | NA | NA | LT AB CABLE IS PROVIDED | No | 1605 DTD 20.09.2021 | Godhra | 2
30 | Arvindbhai K Parmar |  |  | 2021-07-27 | FHO |  |  | VICTIM WENT TO NEAR BY LT BPOLE OF 11KV PAROLI FDR AT VELKOTAR AND GOT SKOCKED | Awaited | NA | NA | LT LINE MAINT. IS CARRIED OUT | NO | GGB/Tech/Accident/9824 dtd 21.09.2021 | Godhra | 2
31 | BUFFALO OWNER-SHRI AVALSING CHIMANBHAI BARIA |  |  | 2021-09-04 | FA |  |  | DUE TO LEAKAGE CURRENT FLOWING FROM BROKEN 11KV PORCELIN PIN INSULATOR'S SPINDLE THROUGH GIRDER POLE. DURING PASSING NEAR GIRDER POLE 02 NOS BUFFALO WAS ELECTROCUTED AND DIED. NAME OF BUFFALO OWNER IS SHRI AVALSING CHIMANBHAI BARIA RESIDENT OF VILL-UMARI | Awaited | NA | NA | MAINTENACE OF FEEDER WITH GUARDING IS CARRIED OUT | No | 2221 DTD 05.09.2021 | Godhra | 4
32 | Buffalo owner Parmar Dahyabhai Mangalbhai |  |  | 2021-09-07 | FA |  |  | DUE TO HEAVY RAIN AND WIND TREE FALLEN ON SERVICE WIRES OF HOUSES AND THERE SERVICE WIRE FALLEN ON SMALL STEEL ROOFED STABLE. AND THIS SMALL STEEL ROOF FALLEN ON BOTH BUFFALOES AND BUFFALOES WERE CAME IN CONTACT WITH LIVE THIS STEEL ROOF AND GOT SHOCKED. | Awaited | NA | NA | Incident is happen duet to cyclone and tree fallen on S/l AND SMALL HUT .Accident happen due to cyclene and treee fallen.new service line is provided . | No | THS/ 2778 DTD:15/9/21 ANDNOD TECH/5006 DTD:18/9/21 | Nadiad | 2
33 | Shri Hartanbhai Chufrabhai Damor (EA) |  |  | 2021-09-08 | NFHD |  |  | While climbing shackle pole(Loc. no,354/14) of Sultanpura tapline of 11 KV Chalali JGY feeder without making off power supply victim came in contact with live conductor got eletrocuted and met with the non-fatal electrial accident | Awaited | NA | NA | MAINT. OF SAME SHACKLE POLE CARRIED OUT | No | VSD/TECH/ACCIDENT/1769 DTD 28.09.2021 | Godhra | 3
34 | Buffalo of Khant Ashwinbhai Rangitbhain |  |  | 2021-09-11 | FA |  |  | The place where buffalo died did not had any leakage current when tested with tester. The buffalo was approx 2 mtr away from LT poles. LT pole didnt had earthing wire. Exact reason unknown. | Awaited | NA | NA | No action required | No | SHR/Tech/6040 DT: 15.09.2021 | Godhra | 8
35 | BUFFALO OF SH. BHALABHAI KALABHAI BHARWAD |  |  | 2021-09-11 | FA |  |  | THE BUFFALO WAS GRAZING & ACCIDENTLY GOT STRANGLED WITH THE STAY WIRE & DISMANTLED THE STAY WIRE FROM GROUND. THE LOOSE STAY WIRE CAME IN CONTACT WITH LIVE 11 KV DO FUSE CONDUCTOR & THE BUFFALO GOT ELECTROCUTED | Awaited | NA | NA | NEW STAY & STAY WIRE PROVIDED | No | 14.09.21 | Baroda O&M | 2
36 | BUFFALO OF SHRI PARMAR SALAMBHAI SHABHAIBHAI |  |  | 2021-09-15 | FA |  |  | As per site situation, Bufflao was passing under TCDP Structure and suddenly fallen down on wet land, Leakage current was not found after power restoration of TC. Actual cause of death may be concluded after PM report. | Awaited | NA | NA | Incident happen due to leakage of current in earthingof transformer,new earthing is reactivated. | No | NOD/TECH/5005 dtd:18/9/2021 | Nadiad | 2
37 | OWNER: MIMKABHAI MANGALIYABHAI BARIYA |  |  | 2021-09-18 | FA |  |  | Due to heavy rain on 25kva jgy village tc of 11KV Poyali feeder earth leakage cureent may be passed. A cow accidentaly went under transformer and got electroculated resulted to death on spot | Awaited | NA | NA | EARTHING OF TRANSFORMER AND MAINT. OF TRANSFORMER IS CARRIED OUT | No | JGD/TECH/2210 18.09.2021 | Godhra | 2
38 | Buffalo of DHANRAJBHAI LALABHAI CHARAN |  |  | 2021-09-19 | FA |  |  | ONE PHASE CONDUCTOR OF OPEN LT OF CHAMAPNER FEEDER WAS BROKEN & 3 NO OF BUFFALO WAS LAYING DEAD ON AND AROUND THE BROKEN CONDUCTOR | Awaited | NA | NA | AB Cable is provided | No | 6016 DTD 01.10.2021 | Godhra | 1
39 | Buffalo of RANJANBEN RAMSINGBHAI RATHOD |  |  | 2021-09-19 | FA |  |  | ONE PHASE CONDUCTOR OF 3Ph 4W LT LINE WAS BROKEN AND BUFFALO GRASING NEAR MIGHT HAVE CAME IN CONTACT WITH LIVE WIRE AND FOUND DEAD AROUND THE BROKEN CONDUCTOR. | Awaited | NA | NA | AB Cable is provided | No | 7810 DTD 01.10.2021 | Godhra | 1
40 | Goat owner PARMAR AMARSINH RAIJIBHAI |  |  | 2021-09-23 | FA |  |  | As per site situation goat passing near the LT pole and electroculated and died current leakage due to heavy rain and cyclone @13:00 hrs phase wire slip from LT pin insulator | Awaited | NA | NA | LT LINE MAINTENANCE IS CARRIED OUT | No | 8.10.21 | Nadiad | 2
41 | BUFFALO OF VASRAMBHAI C BHARWAD |  |  | 2021-09-23 | FA |  |  | AS PER SITE SITUATION BUFFALO PASSING NEAR TC CENTER OF 11 KV CHAMPION FEEDER AND GOT ELECTROCULATED AND DIED DUE TO FAULT CURRENT FOUND FROM INTERNAL WIRING OF WINSOL ENERGY WHICH WAS REFLECTED AT TRANSFORMER CENTER. | Awaited | NA | NA | faulty wiring of consumer side removed. | No | 4955/29.9.2021 | Anand | 2
42 | KALUBHAI RAMSANGBHAI RATHVA |  |  | 2021-09-26 | FA |  |  | SHE MIGHT HAVE CAME IN CONTACT DURING GRACING OF GRAASS NEAR TRANSFORMER CENTER WITH DB & MIGHT HAD GOT LEAKAGAE CURRENT AND DIED | Awaited | NA | NA | MAINTENACE OF FEEDER WITH GUARDING IS CARRIED OUT | NO | 2221 DTD 05.09.2021 | Godhra | 2
43 | COW Owner Mafatbhai Bhikhabhai Rabari |  |  | 2021-09-27 | FA |  |  | the Cow came in contact with Live Earthing Wire of PSC POLE Which became Live Due to Current Leckage from Defective LT PVC CABLE of Transformer | Awaited | NA | NA | REPLACED LTPVC CABLE | No | 30.09.21 | Baroda O&M | 4
44 | BUFFEALO of Sodhabhai Nathabhai Bharwad |  |  | 2021-09-28 | FA |  |  | NO LEACKAGE CURRENT WAS FOUND AT TC DP,EARTHING GI,FABRICATION.AS PER THE PANCHANAMA AT THE TIME OF ACCIDENT,THERE WAS WATER LOGGING OF APPROX. 2 FT AT TC DP DUE TO HEAVY RAIN.SO MIGHT BE LEACKAGE CURRENT FLOWS INSIDE THE WATER LOGGING AND BUFFELO CAME IN CONTACT WITH WATER AND DIED. | Awaited | NA | NA | NO LEAKAGE FOUND | No | 9173/ 29.09.21 | Baroda City | 2

## SOP 03
Name of Distribution Licensee: M G V C L
Quarter : Q-I (July-Aug-Sept- 2021)
Year: 2021-22
REGISTER FOR COMPILING THE COMPLAINTS CLASSIFICATIONWISE Q-I 2021-22
Performa SoP 003 B: |  |  |  | APPENDIX-B (already in the SoP regulation)
Classification | Nature of Complaints | Pending complaints of previous qtr. | Complaints received during the qtr. | Total Complaints =2+3 | No. of Complaints redressed during the quarter. |  |  |  |  | Balance Complaints to be redressed. (4) – (9)
[5 empty] | In stipulated time |  | Beyond stipulated time |  | Total (5) to (8)
[5 empty] | Within 50% of stipulated time. | Within stipulated time. | Up to double the stipulated time | More than double the stipulated time
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
A(i) | Loose Connection | 0 | 82912.2209 | 82912.2209 | 40931.1165 | 41981.1045 | 0 | 0 | 82912.2209 | 0
A(ii) | Intruption due to line Break down | 0 | 53876.1486 | 53876.1486 | 29320.9273 | 24555.2213 | 0 | 0 | 53876.1486 | 0
A(iii) | Intruption due to T/C Fail | 0 | 14087.0797 | 14087.0797 | 7993.8098 | 6093.2699 | 0 | 0 | 14087.0797 | 0
B(i) | Quality of power supply,ordinary case which require no Augmentation | 0 | 11215.1775 | 11215.1775 | 5805.3499 | 5409.8276 | 0 | 0 | 11215.1775 | 0
B(ii) | Quality of power supply,ordinary case which require Augmentation | 0 | 5609.4893 | 5609.4893 | 3194.0003 | 2415.489 | 0 | 0 | 5609.4893 | 0
C(i) | Meters- Stoped/Defective meter | 0 | 15125.7282 | 15125.7282 | 8029.7126 | 7096.0156 | 0 | 0 | 15125.7282 | 0
C(ii) | Meters- Billing on average basis for > two bills | 0 | 9148.4119 | 9148.4119 | 4893.8587 | 4254.5532 | 0 | 0 | 9148.4119 | 0
D(i) | Over head lines - loose wires | 0 | 8517.496 | 8517.496 | 4477.4052 | 4040.0908 | 0 | 0 | 8517.496 | 0
D(ii) | Over head lines - in adiquate ground clearance | 0 | 2016.7059 | 2016.7059 | 1051.9625 | 964.7434 | 0 | 0 | 2016.7059 | 0
E(i) | Bills- for current bills where no addl information required | 0 | 7492.0733 | 7492.0733 | 3054.321 | 4437.7523 | 0 | 0 | 7492.0733 | 0
E(ii) | Bills- for current bills where addl information required | 0 | 3677.5665 | 3677.5665 | 1759.9581 | 1917.6084 | 0 | 0 | 3677.5665 | 0
F(i) | Service connections- where extention of mains is not required | 0 | 10161.1222 | 10161.1222 | 5372.0247 | 4789.0975 | 0 | 0 | 10161.1222 | 0
F(ii) | Service connections- where extention of mains is required | 0 | 3112.5402 | 3112.5402 | 1683.7215 | 1428.8187 | 0 | 0 | 3112.5402 | 0
F(iii) | Service connections- Modification in connected load | 0 | 4081.697 | 4081.697 | 1598.0886 | 2483.6084 | 0 | 0 | 4081.697 | 0
F(iv) | Service connections- Name change/reconnection | 0 | 3940.0467 | 3940.0467 | 1621.6351 | 2318.7616 | 0 | 0 | 3940.3967 | 0
G | Refund of amount due inregard to temp conn | 0 | 764.3407 | 764.3407 | 330.3385 | 434.0022 | 0 | 0 | 764.3407 | 0
H | Others | 0 | 19487.1553 | 19487.1553 | 9546.8676 | 9940.2877 | 0 | 0 | 19487.1553 | 0
| TOTAL | 0 | 255225 | 255225 | 130665.0979 | 124560.2521 | 0 | 0 | 255225.35 | 0
The format is to be sent quarterly
The quarterly reporting of the year means reporting for the period 1st Quarter as Jan – Mar, 2nd Quarter as Apr – Jun, 3rd Quarter as Jul – Sep and 4th Quarter as Oct – Dec of the year.
For any other complaints not mentioned in the classification, the sequence for (H) can be used.

## MG SoP 04
Name of Distribution Licensee: M G V C L
Quarter:II(July-Aug-Sept)
Year: 2021-22
Performa SoP 004 : Publicity carried out while displaying the contact details of consumer complaints centers
Particulars should also cover the details of consumer awareness program conducted, advertisement done through various media like TV, newspaper, radio, pamphlets & booklet distributions, Displays etc. The development of website and any medium through which public education is carried out can be included.
Sr. No | Actions or steps carried out by distribution licensee towards public awareness in the quarter | Likely number of consumers influenced
1 | RTI Officers Name is displayed at customer care centre on each office | 3356148
2 | Necessary information regarding time schedule for new connection and solving complaints is display on the board. | 3356148
3 | Contact nos. of various officers of the company for emergency contact is also displayed at customer care centre. | 3356148
4 | Displayed safety posters at various S/dn,Divisions | 4300
5 | Safety Meeting with Line Staff at various S/dn,Divisions on Every Monday (Line staff influenced) | 14101

## MG SoP 05B
Name of Distribution Licensee: M G V C L
SOP Q-II (July-Aug-Sept-21)
Year: 2021-22
Performa – SoP 005 B: Action taken report by the Redressal Committee
Sr. No | Month | Date and Time Meeting conducted | No of complaints registered at the meeting | No. of complaints pending at the end of the meeting
1 | 1st Month of the quarter (JULY'21) | 15.07.21, 11.00 am at Godhra 23.07.21,11.00 am at Corporate Office | 1+3=4 | 1
2 | 2nd Month of the quarter (Aug'21) | 27.08.21, 11.00 am at Godhra | 3 | Nil
3 | 3rd Month of the quarter (SEPT'21) | 0 | 1 | 1 (Hearing scheduled on dated 20.10.21)

## MG SoP - 06
Name of Distribution Licensee: M G V C L
Financial Year: 2021-22
Quarter : Q-II ( Jul-Aug-Sep-2021 )
Performa SoP 006: Failure of Distribution Transformer
Sr. No. | Name of Circle | Nos. of existing Distribution Transformers at the start of the quarter | Nos. of Distribution Transformers added during the quarter | Total number of Distribution Transformers on end of quarter | Total number of Distribution transformer failed during quarter-II | % failure rate of Distribution transformer
|  | A | B | C=A+B | D | H = (D)*100/C
1 | Baroda O&M | 50078 | 553 | 50631 | 939 | 1.8546
2 | Baroda City | 8727 | 80 | 8807 | 28 | 0.31793
3 | Anand | 23168 | 349 | 23517 | 375 | 1.5946
4 | Nadiad | 30351 | 394 | 30745 | 488 | 1.5872
5 | Godhra | 52678 | 796 | 53474 | 1081 | 2.0215
| MGVCL | 165002 | 2172 | 167174 | 2911 | 1.7413

## SoP008
Name of Distribution Licensee: M G V C L
SOP:Qtr.II(June-July-Aug-21)
Year: 2021-22
Performa SoP 008: Sample Test result for Neutral Voltage
Compliance Sample Test Report for Neutral Voltage
-1 | -2 | -3 | -4 | -5 | -6
Sr. No | Category of consumers | Sample Size | Standard specified in regulation | Deviation of results from the sample test (Numbers) | % age compliance
|  | (Numbers) |  |  | (6) = (5)*100/(3)
| LT consumers | 1457 | 2% | 0 | 0
1 | Domestic | 1026 | 2% | 0 | 0
2 | Commercial | 247 | 2% | 0 | 0
3 | Industrial | 26 | 2% | 0 | 0
4 | Agricultural | 147 | 2% | 0 | 0
5 | Public water works | 11 | 2% | 0 | 0
| HT consumers |  | 2%
6 | HT industrial | 9 | 2% | 0 | 0

## SoP009
Name of Distribution Licensee: M G V C L
SOP:Qtr.II(June-July-Aug-21)
Year: 2021-22
Performa SoP 009: Sample Test result for Voltage variations
Compliance Sample Test Report for voltage variations
-1 | -2 | -3 | -4 | -5
Voltage Level | Sample Size (numbers) | Limit or prescribed standard | Deviation of results from the sample test (Numbers) | % age compliance
(5) = (4)*100/(2)
Low Voltage | 57 | +6% to -6% | 0 | 0
High Voltage | 28 | +6% to -9% | 0 | 0
Extra High Voltage | 1 | +10% to -12.50% | 0 | 0

## SoP010
Name of Distribution Licensee: M G V C L
SOP:Qtr.II(June-July-Aug-21)
Year: 2021-22
Performa SoP 010: Sample Test result for Harmonics
Compliance Sample Test Report for Harmonics
-1 | -2 | -3 | -4 | -5 | -6
Sr. No | Category of consumers | Sample size (Numbers) | Limit or standard prescribed | Deviation of results from the sample test (Numbers) | %age compliance
(6) = (5)*100/(3)
1 | LT consumers | 37 | 3.5% | 0 | 0
2 | HT consumers | 5 | 3% | 0 | 0
3 | EHT consumers | 1 | 3% | 0 | 0
Note: The licensee shall also submit along with the above harmonic data, the records of customer wise drawls of harmonic currents measured at various strategic points.
The formats SoP 008, SoP 009 and SoP 010 have to be sent annually.
For the purpose of annual submissions, the year end has to be considered as the end of December month of a particular year.

## SOP 11A
Quarter II (Jul-Aug-Sept-21)
Year: 2021-22
SoP 011 –A: System Average Interruption Frequency Index (SAIFI)
Sr. No | Month | Ni - Total no of customers for each momentary interruptions | NT - Total no of customers served |  |  | Past year corrosponding Month
1 | 2 | 3 | 4 | 5 | 6=5/4
1 | Jul' 21 | 3134831 | 3364616 | 17158780 | 5.0998 | 5.2915
2 | Aug' 21 | 3101243 | 3342358 | 12839530 | 3.8415 | 7.2342
3 | Sept' 21 | 3162967 | 3352976 | 21513511 | 6.4162 | 4.8904
|  |  | 10059950 | 51511821 | 5.1205 | 5.8053

## SOP 11B
Quarter II (July-Aug-Sept-21)
Year: 2021-22
SoP 011 – B System Average Interruption Duration Index (SAIDI)
Sr. No | Month | ri = Restoration Time for each interruption event | Ni - no of interrupted customers for each sustained interruption event | ri * Ni – Total customer interruption Duration | ri=Restoration Time for each interruption event | Ni= No of Interrupted customers for each sustained Interruption | NT - Total no of customers served | Customer Interruption Duration |  |  | Past year corrosponding Months
[9 empty] | MINS. | HRS.
1 | 2 | 3 | 4 | 5= 3 X 4 | 3 | 4 | 5 | 6 | 7=4/3 | 7A | MINS. | HRS.
1 | Jul' 21 | July |  |  | 905292 | 3134831 | 3364616 | 1117016998 | 331.9894 | 0.23056 | 350.0445 | 0.24306
2 | Aug' 21 | August |  |  | 676529 | 3101243 | 3342358 | 871436784 | 260.7251 | 0.18125 | 420.3379 | 0.29167
3 | Sept' 21 |  |  |  | 969784 | 3162967 | 3352976 | 1306780209 | 389.7374 | 0.27083 | 460.9093 | 0.32014
[6 empty] | 9399041 | 10059950 | 3295233991 | 327.5597 | 0.22778 | 410.4844 | 0.28472

## SOP11C
QuarterII(July-Aug-Sept-21)
Year: 2021-22
SoP 011 – C: Momentary Average Interruption Frequency Index (MAIFI)
Sr. No | Month | Number of Momentary interruptions Imi | Nmi - Total no of customers for each momentary interruptions | NT - Total no of customers served |  |  | Past year corrosponding Month
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | Jul' 21 | 23584 | 2957954 | 3364616 | 40451084 | 12.0225 | 13.4396
2 | Aug' 21 | 19925 | 2918153 | 3342358 | 33451531 | 10.0084 | 14.5545
3 | Sept' 21 | 23906 | 2981781 | 3352976 | 42885902 | 12.7904 | 12.0749
|  |  |  | 10059950 | 116788517 | 11.6093 | 13.3557

## MG_SoP 012
Performa SoP 012 : System Losses at EHT/ 11 KV |  |  |  | JUL-21 TO SEP-21
CALCULATION OF SYSTEM LOSSES AT EHT/ 11 KV
1 | Losses in 11 KV System and Connected Equipment
| i. | Energy Delivered into EHT/ 11 KV and LT Distribution System from EHT/ 11 KV SS (MUs) | A | 6996.729 | Cum Total Sent incl EHT
| ii. | Energy Sold (Billed). EHT direct sales (MUs) | B | 1297.1619 | Cum EHT Sold
| iii. | Energy Sold (Billed) in the 11 KV LT system (MUs) | C | 5089.3195 | Cum TTL Excl EHT-Sold
| iv. | Total Sales (MUs) | (B+C) | 6386.4814
| v. | Losses (MUs) | {(A) - (B+C)} | 610.2477
| vi. | % Losses | {(A) - (B+C)} X 100 / (A) | 8.7219

## MG SoP - 13
Name of Distribution Licensee: M G V C L
Financial Year: 2021-22
Quarter : Q-II ( Jul-Aug-Sep-2021 )
Performa SoP 013: Faulty Meters Replacement
Consumer Category | No. of faulty meters at the start of the quarter | No. of faulty meters added during the quarter | Total no. of defective / faulty Meter | No. of faulty Meters repaired and replaced | No of faulty meters pending at the end of the quarter | Remark
| 1 | 2 | (3)=(2)+(1) | 4 | (5)=(3)-(4)
1 PHASE
MGVCL | 20887 | 16038 | 36925 | 24790 | 12135
3 PHASE
MGVCL | 6423 | 2097 | 8520 | 5025 | 3495
| From MIS-3 Non-Working Meters | 1Ph |  | 3 Ph
|  | Added during month | Replaced during month | Added during month | Replaced during month
| Apr'21 | 9325 | 5703 | 2221 | 1333
| May'21 | 5396 | 4518 | 1401 | 1002
| Jun'21 | 8425 | 6110 | 3813 | 1386
| Q-I | 23146 | 16331 | 7435 | 3721
| Jul'21 | 3928 | 5745 | 524 | 916
| Aug'21 | 5656 | 9630 | 754 | 1818
| Sep'21 | 6454 | 9415 | 819 | 2291
| Q-II | 16038 | 24790 | 2097 | 5025
Oct'21
Nov'21
Dec'21
| Q-III | 0 | 0 | 0 | 0
Jan'22
Feb'22
Mar'22
| Q-IV | 0 | 0 | 0 | 0

## MG_SoP 014
| Performa SoP 014: Statement Showing the ATC losses, collection efficiency and Billing Efficiency | [8 empty] | F.Y. 2021-22
| Quarter | Month | Units Input (MUs) | Units Billed (MUs) | Billing Efficiency % | Revenue Billed (Rs. Crs) | Revenue Collected (Rs. Crs) | Collection Efficiency % | Business Efficiency % | ATC Loss%
Sr No |  |  | A | B | C = (B/A)*100 | D | E | F = (E/D)*100 | G = (C*F)/100 | H = 100 - G
Q-I | Q-I | April'21 | 1246.711 | 1086.2582 | 87.1299 | 686.57 | 612.77 | 89.2509 | 77.7642 | 22.2358 | 160.4528 | 12.8701
Q-I |  | May'21 | 1172.5739 | 1057.0496 | 90.1478 | 749.64 | 663.51 | 88.5105 | 79.7903 | 20.2097 | 115.5243 | 9.8522
Q-I |  | June'21 | 1127.2341 | 1082.643 | 96.0442 | 731.64 | 719.91 | 98.3968 | 94.5044 | 5.4956 | 44.5911 | 3.9558
Q-I |  | Q-I | 3546.519 | 3225.9508 | 90.961 | 2167.85 | 1996.19 | 92.0816 | 83.7583 | 16.2417 | 320.5683 | 9.039
Q-II | Q-II | July'21 | 1202.7921 | 1071.1743 | 89.0573 | 757.52 | 767.77 | 101.3531 | 90.2623 | 9.7377 | 131.6179 | 10.9427
Q-II |  | August'21 | 1191.5756 | 1060.6757 | 89.0146 | 778.04 | 762.81 | 98.0425 | 87.2721 | 12.7279 | 130.8999 | 10.9854
Q-II |  | September'21 | 1055.8423 | 1028.6806 | 97.4275 | 776.9 | 771.82 | 99.3461 | 96.7904 | 3.2096 | 27.1616 | 2.5725
Q-II |  | Q-II | 3450.21 | 3160.5306 | 91.604 | 2312.46 | 2302.4 | 99.565 | 91.2055 | 8.7945 | 289.6794 | 8.396
Half Year | 2021-22 | Half Year | 6996.729 | 6386.4814 | 91.2781 | 4480.31 | 4298.59 | 95.944 | 87.5759 | 12.4241 | 610.2477 | 8.7219
Q-III | Q-III | October | -6996.729 | -6386.4814 | 91.2781 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | -610.2477 | 8.7219
Q-III |  | November | 0 | 0 | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0!
Q-III |  | December | 0 | 0 | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0!
Q-III |  | Q-III | -6996.729 | -6386.4814 | 91.2781 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | -610.2477 | 8.7219
Q-IV | Q-IV | January | 0 | 0 | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0!
Q-IV |  | February | 0 | 0 | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0!
Q-IV |  | March | 0 | 0 | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0!
Q-IV |  | Q-IV | 0 | 0 | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0!
Total | 2021-22 | Total | 0 | 0 | #DIV/0! | 4480.31 | 4298.59 | 95.944 | #DIV/0! | #DIV/0! | 0 | #DIV/0!
Month | Cumm. Sent | Cumm. Sold | Month Sent | Month Sold
Apr | 1246.711 | 1086.2582 | 1246.711 | 1086.2582
May | 2419.2849 | 2143.3078 | 1172.5739 | 1057.0496
Jun | 3546.519 | 3225.9508 | 1127.2341 | 1082.643
Jul | 4749.3112 | 4297.125 | 1202.7921 | 1071.1743
Aug | 5940.8868 | 5357.8007 | 1191.5756 | 1060.6757
Sep | 6996.729 | 6386.4814 | 1055.8423 | 1028.6806
Oct |  |  | -6996.729 | -6386.4814
Nov |  |  | 0 | 0
Dec |  |  | 0 | 0
Jan |  |  | 0 | 0
Feb |  |  | 0 | 0
Mar |  |  | 0 | 0

## SoP_15(Modified)
Performa SoP 015: Release of New Connection status for FY 2021-22
Qtr | Consumer category | Total no. of consumers connected at the beginning of half-year/year | Pending at the Beginning of the of the Half year/year | New Applications received during the half-year / year | No. of connections released during the half-year / year | No. of applications pending at the end of half-year / year | Total no. of consumers connected at the end of half-year/year
1st Half (Apr-May-Jun-Jul-Aug-Sep) | Domestic | 2724603 | 823 | 34517 | 29451 | 1084 | 2754054
| Commercial | 382044 | 354 | 8553 | 6564 | 449 | 388608
| Industrial LT | 10403 | 56 | 900 | 748 | 133 | 11151
| Agriculture (Total) | 172509 | 12473 | 3849 | 3410 | 12905 | 175919
| Industrial HT | 2533 | 63 | 101 | 115 | 49 | 2648
| Total | 3292092 | 13769 | 47920 | 40288 | 14620 | 3332380
2nd Half (Oct-Nov-Dec-Jan-Feb-Mar) | Domestic | 2754054 | 1084 | #REF! | #REF! | #REF! | #REF!
| Commercial | 388608 | 449 | #REF! | #REF! | #REF! | #REF!
| Industrial LT | 11151 | 133 | #REF! | #REF! | #REF! | #REF!
Agriculture (Total)
Industrial HT
| Total | 3153813 | 1666 | #REF! | #REF! | #REF! | #REF!
Annual | Domestic | 2724603 | 823 | #REF! | #REF! | #REF! | #REF!
| Commercial | 382044 | 354 | #REF! | #REF! | #REF! | #REF!
| Industrial LT | 10403 | 56 | #REF! | #REF! | #REF! | #REF!
Agriculture (Total)
Industrial HT
| Total | 3117050 | 1233 | #REF! | #REF! | #REF! | #REF!

## MG SoP 16
Name of Distribution Licensee: M G V C L
Quarter : Q-II ( JULY.-AUG.-SEP.- 2021)
Year: 2021-22
Performa SoP 016: Compensation details
COMPENSATION DETAILS
Sr.No. | Event | Compensation | No of cases where compensation was given (in numbers) | Amt of compensation paid (in Rs.)
1 | Duty to provide supply | Rs. 50 per day of delay from the limit specified in the performance regulations | 0 | 0
| a) New Connection |  | 0 | 0
| b) Additional Load |  | 0 | 0
| c) Temporary supply |  | 0 | 0
| d) Shifting service connection |  | 0 | 0
| e)Transfer of service connection |  | 0 | 0
| f) Change in tariff category of consumer |  | 0 | 0
2 | Complaints in billing | Rs. 50 for non reply within the period prescribed in Regulations | 0 | 0
3 | Replacement of meters | LT- Rs. 25 per day of delay - maximum Rs.2,500 and HT - Rs. 250 per day of delay - maximum of Rs.5,000 | 0 | 0
4 | Interruption of supply | LT- Rs. 25 for every 6 hrs of delay- maximum of Rs. 500 and HT- Rs. 50 for every 6 hrs delay- maximum Rs. 1000/- | 0 | 0
5 | Voltage fluctuations and complaints | Rs. 50 for failure to visit or convey findings within the stipulated period | 0 | 0
6 | Responding to consumer's complaints | Rs. 25 for each day of delay- maximum Rs. 500 | 0 | 0
7 | Grievance Handling | Rs.25 for failure in handling grievance | 0 | 0
TOTAL |  |  | 0 | 0