## MG COVER PAGE
Name of Distribution Licensee: M G V C L
Quarter : Q-II (July-Aug-Sept- 2022)
Year: 2022-23

## MG SoP 01
Name of Distribution Licensee: M G V C L
QuarterII (July-22 to Sept-22)
Year:2022-23
Performa - SoP 001: Fatal and Non-Fatal electrical accident report
NUMBER OF ACCIDENTS FOR THE 1st QUARTER OF 2022-23
Sr.No | Name of Area/Circle | No of accidents in the quarter |  |  |  |  | Cumulative since the first quarter of the current FY 2022-23
|  | Departmental |  | Outside |  |  | TOTAL
|  | FH | NFH | FH | FA | NFH | FH | FA | NFH
1 | Baroda (City) | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0
2 | Baroda (O&M) | 0 | 2 | 5 (1-Pvt) | 14 | 1 | 6 (1-Pvt) | 15 | 7
3 | Anand | 0 | 0 | 2 | 1 | 0 | 2 | 3 | 1
4 | Godhra | 0 | 0 | 9 (5-Pvt) | 18 (1-Pvt) | 3 | 15 (9-Pvt) | 21 (2-Pvt) | 4
5 | Nadiad | 0 | 1 | 2 | 15 | 2 | 8 (2-Pvt) | 19 | 8
| TOTAL | 0 | 3 | 19 (6-Pvt) | 48 (1-Pvt) | 6 | 32 (12-Pvt) | 58 (2-Pvt) | 20
FH – Fatal Human, FA – Fatal Animal, NFH – Non-fatal Human | [5 empty] | 76 |  |  | 110
PVT - Private Premises Accident.

## SoP 002
Performa – SoP 003: Action taken report for safety measures complied for the electrical accidents occurred
ACTION TAKEN REPORT FOR SAFETY MEASURES COMPLIED FOR THE ELECTRICAL ACCIDENTS OCCURED IN THE FIRST QUARTER OF FY 2022-23
1 | 2 |  |  | 3 | 4 |  |  | 5 | 6 | 7 | 8 | 9 | 10
Sr. No | Location of Accident and details of the victim | Address | sdn | Date of occurrence | Type of Accident | Installation | Accident Type | Cause of Accident | Findings of CEI / EI / AEI | Remedies suggested by CEI /EI / AEI in various cases | Whether the remedy suggested is complied | Action taken to avoid recurrence of such Accident | Circle office
1 | Driti Sanjaykumar Rana,Ranavas,Vill-Santrampur Town,Ta-Santrampur,Dist-Mahisagar |  |  | 2022-06-26 | NFHO |  |  | Heavy cyclone with heavy rain was there,during the cyclone with rain, the service line wire might have touched with GI wire with Girder pole. Girl Child playing outside of his house during rain and she touched the girder pole and get electro shock | AWAITED | NA | NA | Nil | Godhra
2 | Rajubhai Ramabhai Bharvad,Near Industrial compund,Vill-Alindra,Ta-Kalol,Dist-Panchmahal |  |  | 2022-07-02 | FA |  |  | HAVE RAIN &WIND THE TREE BRANCHES FALEN ONLINE < ABC CARRIER WIRE TO POLE GI WIRE ONTC DP POLE SAME TIME SHE CAME ON CONTACT A7DIED | AWAITED | NA | NA | TC AND LINE MAINT. IS CARRIED OUT. EARTHING OF TC AND POLE IS REACTIVATED. | Godhra
3 | Thakor Ranjitbhai Mathurbhai,at Moti bar,Vill-Moti Bar,Ta-Virpur,Dist-Mahisagar |  |  | 2022-07-03 | FHO-Pvt |  |  | As per statement of eyevitness statement, victim tries to use unthourised electric power using jointed private wire from nr. by AG connection of Shri Raval Mathurbhai Dalabhai. Accidentally victim touched thi | AWAITED | NA | NA | Nil | Godhra
4 | Cow off Manishbhai Sodabhai Bharvad,Near Rampura sabu ni muvadi tc centre,Vill-Rampura,Ta-Galteshwar,Dist-Kheda |  |  | 2022-07-06 | FA |  |  | AN ACCIDENT OCCURRED DUE TO THE SERVICE LINE OF SINGLE PHASE CONSUMER OF RAULAJI DHARMENDRASINH KHUMANSINH WAS BROKEN AND TOUCHED TO GI WIRE AND CURRENT LEAKAGE HAPPENED AND AT THAT COW WAS PASSING UNDER THE TC CENTER AND HENCE IT WAS ELECTROCULATED AND D | AWAITED | NA | NA | the service line is replaced and leakage of current was removed | Nadiad
5 | Bullock of Jagabhai Kesarbhai Maliwad, Near Simtal area farm ,Vill-Kaduchi,Ta-Santrampur,Dist-Mahisagar |  |  | 2022-07-08 | FA |  |  | THE BULLOCK STRUCK BY LIGHTNING FROM NEARBY ELECTRIC POLE AND IT GOT ELECTROCUTED DUE TO WET SOIL. THE INSULATION OF CABLE WAS BROKEN, WHICH RESULTED THE LEAKAGE CURRENT TO PASS THROUGH GI EARTHING WIRE. | AWAITED | NA | NA | Nil | Godhra
6 | Buffalo owner : Harun Rashid Mohamad Alam,Lilesara road,Vill-Lilesara,Ta-Godhra,Dist-Panchmahal |  |  | 2022-07-09 | FA |  |  | PM report and Police panchnama was received at sdn office from Vetenary Officer on dated 20/7/22, no complaint was received at sdn office. On dated 21/7/22 said locationwas visited by DE & JE of sdn and panchnamu was done. Accident place shown by owner w | AWAITED | NA | NA | TC AND LINE MAINT. IS CARRIED OUT. | Godhra
7 | Cow of shri Shankarbhai Ramshingbhai Rabari,Near pani ni tanki,Vill-Sokhada,Ta-Vadodara,Dist-Vadodara |  |  | 2022-07-09 | FA |  |  | COW OF SH. SHANKARBHAI RAMSHINGBHAI RABARI WHILE GRAZING CONDUCTOR OF 11KV VASNA AGDOM FEEDER SNAPPED ON COW AND ELECTROCUTED AND DIED | Awaited | NA | NA | Line Maintenance work done | Baroda O&M
8 | Buffalow of Shri Arvindbhai Shanabhai Raval,pij-ramol road, near chhapi bhagol,Vill-Pij,Ta-Vaso,Dist-Kheda |  |  | 2022-07-09 | FA |  |  | The buffalow coming from Pij Ramol road and eating grass near transformer centre of Palana AG feeder . That time buffalow's hind lag stucked in stay wire of stay and stay wire touched live Do fuse (bottom side) and came directly touched the live DO an | AWAITED | NA | NA | Stay wire position ractified. | Nadiad
9 | Sullathusen Firojbhai Metar- buffelow,Rida park society,Vill-Halol,Ta-Halol,Dist-Panchmahal |  |  | 2022-07-10 | FA-Pvt |  |  | AS PER SITE VISIT LT ABC AND NAGAR PALIKA PRIVATE STREET LIGHT WIRE IS PASSING ON A POLE AT RIDA SOCIETY. DUE TO IRON FIXTURE STREET LIGHT SHORT AND PSC POLE GI EARTHING WIRE TOUCHED WITH IRON FIXTURE(NAGAR PALIKA PRIVATE STREET LIGHT) AND LEAKAGE CURREN | AWAITED | NA | NA | NA | Godhra
10 | Buffalo of Dipsang Ranchhod Makwana,Vastana-laxmipura road,Vill-Vastana,Ta-Matar,Dist-Kheda |  |  | 2022-07-10 | FA |  |  | At Accident place buffalo eating some grass in farm near transformer centre. At time heavy rain with wind pressure Buffalo contact with earrthing wire of transformer and got electric shock and died on | AWAITED | NA | NA | FIRED LT AB CABLE REMOVED FROM CONTACT WITH TC EARTHING WIRE | Nadiad
11 | She Buffalow of Shri Lalabhai Vajabhai Pagi,Behind chapri bus stand,Vill-Chapri,Ta-Lunavada,Dist-Mahisagar |  |  | 2022-07-10 | FA |  |  | at time of site visit it was came to notice that, there was no any leakage current was found at the location. But as per eye witness there was a rain @ 10.00 am and the she buffalo came near the TCDP and LT pole . The she buffalo may came in | AWAITED | NA | NA | NIL | Godhra
12 | Calf owner Shankrabhai Savlabhai Ganava,Near Ambakach nishal fly,Vill-Ambakach,Ta-Dhnapur,Dist-Dahod |  |  | 2022-07-10 | FA |  |  | During Primary investigation on spot it has to come to notice that the calves was wondering near transformer center. The calves may be come in contact with transformer center PSC pole or | AWAITED | NA | NA | TC AND LINE MAINT. IS CARRIED OUT. | Godhra
13 | Buffalo of Shri Vikrambhai Kukabhai Bharvad,Nr Shedhi river farm,Vill-Dakor,Ta-Thasra,Dist-Kheda |  |  | 2022-07-11 | FA |  |  | ON DATE 11.07.2022 AT AROUND 10:00 HRS, R PHASE CONDUCTOR SLIPPED FROM PIN BINDING AT PIN POLE NO. UMR/DKR/141 DUE TO PIN INSULATOR PUNCTURE (OLD PORCELAIN), SO CONDUCTOR WAS HANGED FROM POLE TO GROUND AND DURING THAT TIME BUFFALOS WERE COMING FOR | AWAITED | NA | NA | THE FAULTY PIN WAS REPLACED AND STRINGGING OF CONDUCTOR WAS CARROUT AND TREE CUTING WAS ALSO DONE | Nadiad
14 | Shri Kanubhai Vitthalbhai Solanki,at Dashrath,Vill-Dashrath,Ta-Vadodara,Dist-Vadodara |  |  | 2022-07-11 | FHO-Pvt |  |  | There is a shop of Sh. Bipinbhai Chandubhai Solanki Consumer No. 02103/04449/5 at Dashrath with iron shade in front side LED bulb was hung through iron shade for night lighting after main switch of consumer (private wiring) primises. | Awaited | NA | NA | Private Wiring premises so no actions needed of MGVCL | Baroda O&M
15 | Buffalo owner of Shri Ramanbhai Somabhai Vasava,Nr canal varsada to itola road,Vill-Varsada,Ta-Vadodara,Dist-Vadodara |  |  | 2022-07-12 | FA |  |  | As per site visit, on date 12.07.2022, 11kv Itola ag feeder varasada to Itola at main canal crossing on one side shackle pole one conductor broken and at same time buffalo was passing from there, which was contact with line and got electr | AWAITED | NA | NA | RE-STRINGING OF CONDUCTOR AS PER NORM AND NOW QUALITY OF REPAIRED AT LOCATION WHERE ACCIDENCT OCCURRED | Baroda O&M
16 | Sh. Laxmanbhai Budhabhai Chauhan, Sh. Yogeshbhai Pravinbhai Parmar and Sh. Javansinh Punambhai Dabhi,Kachhai khadiya vistar in farm of kanubhai chandabhai dabhi,Vill-Kachhai,Ta-Mehmadabad,Dist-Kheda |  |  | 2022-07-12 | NFHO |  |  | SOME PERSONS CARRY OUT TREE CUTTING WORK ON 11 KV KACHHAI AG FDR. TAPLINE AFTER DROPPING D.O FUSE. DURING TREE CUTTING ONE CONDUCTOR SNAPPED. HENCE, THEY WERE TRYING TO JOINT THIS CONDUCTOR. DURING THAT WORK THIS SNAPPED CONDUCTOR TOUCHED TO 11 KV KHAMBH | AWAITED | NA | NA | Village wiremen informed toi 132 KV Mbad SS Operator to not restart the 11 KV Khambhali JGY | Nadiad
17 | Tusharbhai Laljibhai Rabari,Palol village near bachli mataji temple,Vill-Palol,Ta-Sojitra,Dist-Anand |  |  | 2022-07-12 | FHO |  |  | Fabricated Vehical EICHER.of 12 feet parked under 11 kv Palol AG line and Victim height of 5 feet was standing on fabricated body so Clearence did not remain of | Awaited | NA | NA | No action required | Anand
18 | Shri Ajithkumar Murthi Christian,at Vemali ,Vill-Vemali,Ta-Vadodara,Dist-Vadodara |  |  | 2022-07-13 | FHO |  |  | Sh. Ajithkumar Murthi Christian driver of truck no TN 64 W5564 after loading material from padmavati road lines parked his vehicle under 11KV line. He climbs on roof for wraping "Tarpaulin" and accidentally touched the live wire of 11KV V | AWAITED | NA | NA | THIS ACCIDENT OCCURS DUE TO LOADED TRUCK AND PERSON IS ON LOADED TRUCK | Baroda O&M
19 | Tanmay H Panchal,DODP Structure Nan/3/Gpl2/Ind/13&14 ,Vill-Ranoli,Ta-Vadodara,Dist-Vadodara |  |  | 2022-07-13 | NFHD |  |  | AFTER COMPLETION OF JUMPERING WORK ON DODP STRUCTURE LOC NO NAN/3/GPL2/13&14 OF INDUSTRIAL FEEDER NAMED GPL-2 FOR CHANGEOVER WORK.DUE TO RETURN CURRENT FROM UNKNOWN SOURCE HE HAD ELECTRIC SHOCK. | AWAITED | NA | NA | Mantenance work done and also informed to companies of GIDC | Baroda O&M
20 | Solanki Kinjalben Karansinh,Solanki faliyu,Vill-Ratanpur reliya,Ta-Godhra,Dist-Panchmahal |  |  | 2022-07-14 | NFHO |  |  | AS VICTIM CAME IN CONTACT WITH METTALIC SHED WHICH IS BROKEN DUE TO PARAFIT FALLEN ON SERVICE LINE AND SHE MAY GOT ELECTRIC CUR | AWAITED | NA | NA | NA | Godhra
21 | She-Buffalo Gulabsinh Shanabhai Parmar,In the farm of shri takhatsinh manabhai chauhan,Vill-Alali,Ta-Kalol,Dist-Panchmahal |  |  | 2022-07-14 | FA |  |  | Victim came in contact with dead LT line(AB Cable) of Vacchavad JGY fdr, got electric shock and met with fatal electrical accident. The LT Line might have came in contact with 11 KV Khadki AG fdr passing over due to tightening of LT line AB | AWAITED | NA | NO | MAINTANACE & RECTIFICATION DONE | Godhra
22 | Buffalo of Jalbhai Bakorbhai Chavda,Near jio tower at bhagol,Vill-Sisodiya pura,Ta-Savli,Dist-Vadodara |  |  | 2022-07-14 | FA |  |  | SH MAHENDRABHAI JALABHAI CHAVDA WHILE GRAZING THE BUFFALOES IN THE FARM NEAR BHAGOL VIILL SISODIYAPURA.BUFFALO WAS WENT NEAR 100KVA TRANSFORMER STRUCTURE & ELECTROCUTED AND DIED DUE TO RETURN CURRENT IN NEUTRAL STRIP EARTHING FROM LT NETWORK. | AWAITED | NA | NA | LT ABC Insulation coated and rectified. | Baroda O&M
23 | Sarabhai Sandhabhai Bharvad,Rajubhai chhagnbhai na khetr ma,Vill-Naranpura,Ta-Kalol,Dist-Panchmahal |  |  | 2022-07-14 | FA |  |  | h t LINE POLE OF 1 KV NARANPURA AG FDR | AWAITED | NA | NA | LINE MAINT. IS CARRIED OUT | Godhra
24 | Buffalo owner name-Ramsinh Juvansinh Gohel,Udapura kathlal-kapadwanj road,Vill-Udapura,Ta-Kapadwanj,Dist-Kheda |  |  | 2022-07-16 | FA |  |  | ON DATED-16.07.2022 DUE TO RAIN MIDDLE CONDUCTOR OF THREE PHASE FOUR WIRE LT LINE BROKEN AND FALL ON BUFFALO LAYING BELOW LT LINE AND DIED | AWAITED | NA | NA | POWER SUPPLY MADE OFF IMMEDIATELY | Nadiad
25 | Shri Gandhi Tusharbhai Virendrabhai,1-rajeshwar res,Vill-Vadodara,Ta-Vadodara,Dist-Vadodara |  |  | 2022-07-16 | FHO |  |  | DUE TO UNAUTHORISED CONSTRUCTION OF VICTIM HOUSE SO DISTANCE BETWEEN HOUSE AND 11 KV LINE IS VERY LOW SO ON TARRACE VICTIM IN CONTACT WITH LIVE 11 KV CONDUCTOR AND GOT ELECTROCUTED AND | AWAITED | NA | NA | KSD/ 4421 DTD. 18.07.22 NOTICE ISSUD FOR ILLEGAL CONSTRUCTION. ESTIMATE OF RS. 147884/- ISSUED ON 6.08.22. UNDER PAYMENT. | Baroda City
26 | Male buffalo(bull) of Shri Jalam Fata Parmar,at Vadali(hemtaji na muvada),Vill-Vadali (hemtaji na muvada),Ta-Kapadwanj,Dist-Kheda |  |  | 2022-07-17 | FA |  |  | ON DATED 17.07.2022 AROUND 16:30 HRS RAIN WAS FALLING WITH HEAVY WIND IN VILLAGE VADALI (HEMTAJI NA MUVADA). DUE TO THAT A BIG TREE’S BRANCH FALLING ON VILLAGE LT LINE OF 11 KV DANTALI JGY FEEDER RESULTING INTO SNNAPING OF CONDUCTOR AND AT THAT TIME LITT | AWAITED | NA | NA | FOR SAFETY PURPOSE TRANSFORMER POWER SUPPLY MADE OFF | Nadiad
27 | Buffalo owner: Baria Prabhatsinh Andarsinh,Near kotar,Vill-Ghoghadva,Ta-Halol,Dist-Panchmahal |  |  | 2022-07-18 | FA |  |  | a ht pole dp structure of 11kv vadia ag feeder was broken due to erosion of bail , the Ht line in AG land, a buffalo contacted with live wire during gracing and died on the spot | AWAITED | NA | NA | NEW DO ODP STRUCTURE ERECTED ,NEW EARTHING DONE | Godhra
28 | Cow of Prabhatbhai Zaverbhai Bariya,At kadachala-zampa,Vill-Kadachala,Ta-Bodeli,Dist-Chotaudepur |  |  | 2022-07-19 | FA |  |  | Due to heavy wind and rain LT shackle insulator of LT line get unbind from U clamp and LT wire come in contact with U clamp which cause return current in line and passed through transformer earthing | AWAITED | NA | NA | LT shackle insulator replaced and maintenace carried out. | Baroda O&M
29 | Cow of Samuben Jagdishbhai Rabari,Opp. Rachana davakhana,Vill-Bhadarwa,Ta-Savli,Dist-Vadodara |  |  | 2022-07-19 | FA |  |  | SAMUBEN JAGDISHBHAI RABARI'S COW WAS ELECTROCUTED AND DEAD DUE TO STREET LIGHT LIVE DETORIATED CONDUCTOR IS LAYED OVER LT GIRDER POLE OF JGY RANIYA FEEDER. | AWAITED | NA | NA | Inslulaton jumper work done. | Baroda O&M
30 | Buffalo of Parmar Sursangbhai Gotabhai,Nandoli khandhli road ,Vill-Nandoli,Ta-Matar,Dist-Kheda |  |  | 2022-07-20 | FA |  |  | at the accident place buffalo was eating grass near transformer center and suddenly fall down between two psc pole of transformer and died on the spot.No any reason found about these accident during s | AWAITED | NA | NA | POWER SUPPLAY OFF | Nadiad
31 | Cow of Kamleshbhai Babubhai Talpada,Laxmipura,Vill-Vadthal,Ta-Mahudha,Dist-Kheda |  |  | 2022-07-22 | FA |  |  | Possibility of current passed through GI wire of earthing due to creepers on transformer centre | AWAITED | NA | NA | Earthing reactiveted | Nadiad
32 | Savitaben Kalubhai Gamar (cow owner), at Ranivav,D'baria,Vill-Devgadhbaria,Ta-Devgadhbaria,Dist-Dahod |  |  | 2022-07-23 | FA |  |  | The accident cow was grezing at location,then suddenly there was rainning and so cow got scared and ran away,hence its horn cought in the guy wire.therefore,it is possibility of induction current pass through the guy wire.and it might be cow | AWAITED | NA | NA | LINE MAINTENACE WORK DONE | Godhra
33 | She buffalo of Khant Khodabhai Ravjibhai,Near panchayat water tank Gajani talav road,Vill-Katakpura,Ta-Mehmadabad,Dist-Kheda |  |  | 2022-07-25 | FA |  |  | BUFFALO PASSING NEARBY TRANSFORMWER GOT TOUCH WITH NEUTRAL WIRE OF AG TRANSFORMER FROM WHICH LEAKAGE CURRENT WAS PASSING AND ELECTROCUTED. | AWAITED | NA | NA | DO FUSES OF TRANSFORMER HAS BEEN OPENED. | Nadiad
34 | Cow of Rabari Ankurbhai Shankarbhai,Near bhilapur police stationat,Vill-Bhilapur,Ta-Dabhoi,Dist-Vadodara |  |  | 2022-07-25 | FA |  |  | ON DATE 25.07.2022 AT 10.30 AM COW OF RABARI ANKURBHAI SHANKARBHAI GRAZING NEAR AG TC OF ASHOK RODIYA & TC CENTER IS FULL OG WATER LOGGED SO MAY DUE TO LEAKAGE OF CURRENT THROUGH EARTHING & COW MAY COME IN CONTACT WITH EARTHING WIRE & GOT ELECROCUTE | Awaited | NA | NA | Distribution Box maintenance work carried out | Baroda O&M
35 | Cow of Sanjaykumar Chatrasinh Darbar,at Indira nagri,Vill-Piplag,Ta-Nadiad,Dist-Kheda |  |  | 2022-07-26 | FA |  |  | Contractor working for new Line HT ABC stringing work at tapping side one sapn is stringing on existing LT Line pole with help of angle and hook due to rain starting contractor work stop and supply of LT Line make on nd at that time one phase of 3ph serv | RECEIVED | Electric asset to be maintained regularly for safty purpose. | YES | Replaced punctured service wire emiditaly | Nadiad
36 | Buffalo owner Shri Jayeshkumar Jamnadas sadhu,Limdi -Ramji madir road,Vill-Limdi,Ta-Zalod,Dist-Dahod |  |  | 2022-07-27 | FA |  |  | At the time of site visit no direct leakage current found on the pole but accident might be occure due to induction current in wet ground. | AWAITED | NA | NA |  | Godhra
37 | DHARMENDRASINH KARANSINH MAHIDA, Vill-Natvarnagar, Tal-Savli, Dist-Vadodara |  |  | 2022-08-11 | FHO |  |  | VICTIM'S DEAD BODY WAS FOUND NEAR TCDP STRUCTURE AND AT THE TIME OF INVESTIGATION BY ENGINEERS AND LINE INSPECTORE,THERE IS NO ANY LEAKAGE CURRENT AND ELECTRIC SUPPLY IN STAY WIRE AS WELL AS AT TCDP STRUCTURE AND IN EARTHING. | Awaited | NA | NA | OUTSIDER,THERE IS NO ANY LEAKAGE CURRENT AND ELECTRIC SUPPLY IN STAY WIRE AS WELL AS AT TCDP STRUCTURE AND IN EARTHING. | Baroda O&M
38 | MEDA PRAVINBHAI BACHUBHAI'S GOATS, Vill-KHAREDI, Tal/Dist-Dahod |  |  | 2022-08-12 | FA |  |  | GOATS WERE WONDERING NEAR TC CENTRE AND LAND WAS WET DUE TO RAIN, THE GOATS MAY CAM E IN CONTACTS WITH TC POLE AND GOT ELECTROCUTED, NO LEAKAGE CURRENT FOUND NEAR TC CENTRE | AWAITED | NA | NA | TC AND LINE MAINT. IS CARRIED OUT. | Godhra
39 | SHE BUFFALO (OWNER NAME: PARMAR KANTABEN CHANDRASINH, Vill-NAVAGHARA, Tal-Godhra , Dist-Panchmahal |  |  | 2022-08-12 | FA |  |  | AS BUFFALO CAME IN CONTACT WITH LIVE LT BROKEN CONDUCTOR BUFFALO GOT ELECTROCUTED AND DIED ONSPOT | AWAITED | NA | NA | LT LINE MAINTENACE WORK DONE | Godhra
40 | Cow Owner : Malabhai Mohanbhai Bharwad, Vill-Kherwadi. Tal-Waghodia, Diat-Vadodara |  |  | 2022-08-13 | FA |  |  | Shri Malabhai Mohanbhai Bharwad while grazing the cows in the farm in Kherwadi village, R phase insulationof cable got damaged and got touch with earth wire and cow came in contact with earth wire and cow came in contact with earth wire and got electrocut | Awaited | NA | NA | ITS IN CONSUMER PREMISE AND EARTHING CABLE WORK DONE BY CONSUMER | Baroda O&M
41 | Buffalo of Naginbhai Himmatbhai Rathod, Vill-Vasna Kotaria, Tal/Dist-Vadodara |  |  | 2022-08-15 | FA |  |  | Sh Nagjibhai himmatbhai rathod grazing the buffelo in the farm at Kumari vago faliya village: Vasna kotariya, Conductor of LT line of AG line snapped and buffelo came in contact due to wet land and electrocuted and died. | Awaited | NA | NA | Conductor rejoint and stringing | Baroda O&M
42 | Buffalo Owner : Bathabhai Butabhai Bharwad, Ganpatpura Prathmik Shala, Vill-Ganpatpura, Tal-Waghodia, Dist-Vadodara |  |  | 2022-08-16 | FA |  |  | Shri Bathabhai Butabhai Bharwad while grazing the buffalo in the farm in Ganpatpura village behind Ganpatpura Prathmik Shala , service wire got in touch to weather shed of consumer no. 02907/00029/2 and leakage current at earthwire at transformer and buff | Awaited | NA | NA | REPLACED FAULTY CABLE | Baroda O&M
43 | COW OF SHRI. MALJIBHAI MELABHAI DESAI, Vill-TAIYABPURA (DABHI FALIYA), Tal-Kapadvanj, Dist-Kheda |  |  | 2022-08-17 | FA |  |  | ON DATED-17.08.2022 AROUND 06:45 AM AT VILL-TAIYABPURA (DABHI F) ACCIDENTALLY TREE BRANCH FALLEN DUE TO RAINY SEASON AND FALL DOWN ON SERVICE LINE OF BHAILALBHAI CHANDUBHAI THAKOR'S RGP CONNECTION RESULTING INTO MINOR BREAKAGE AND LEAKAGE OF CURRENT FOUND | AWAITED | NA | NA | FOR SAFETY PURPOSE VILLAGE TRANSFORMER POWER SUPPLY MADE OFF | Nadiad
44 | AMALIYAR DHARMENDRABHAI RAMESHBHAI, Vill-KHAREDI, Tal/Dist-Dahod |  |  | 2022-08-17 | FHO |  |  | AS PER EYE WITNESS VICTIM WAS ARRANGING GREEN GRASS ON CRUSER VEHICAL AND SUDDENLY BY VICTIM'S MISTAKE GREEN GRASS CONNECTED WITH 11KV LINE AND VICTIM GOT ELECTROCUTE. AT TIME OF INVESTIGATON NO ELECTRIC DOTS FOUND ON LINES AND GREEN GRASS ASLO NO TRIPPIN | AWAITED | NA | NA |  | Godhra
45 | KAILESH M. MAVI, Vill-Rania, Tal-Savli, Dist-Vadodar |  |  | 2022-08-17 | NFHD |  |  | KAILESH M MAVI WAS CARRIED OUT REJUMPERING WORK OF 11KV INNARCO IND FEEDER AT LOC OPPOSITE SANTRAM TAMPLE. DURING REJUMPERING WORK HE WAS ELECTROCUTED BY ELECRIC SUPPLY.SO HE INJURED ON THE POLE.HE GOT INJURED IN BOTH HAND AND IN BOTH LEG. | Awaited | NA | NA | Insulation jumper work done. | Baroda O&M
46 | Shri Jalambhai Bhathibhai Parmar(Age-75 yrs) & Dipakbhai Gulabbhai Parmar(Age-24 Yrs), Sardarpura Faliya, Vill-Bhalania, Tal-Godhra, Dist-Panchmahal |  |  | 2022-08-17 | FHO-Pvt |  |  | On the day of incident both the victim might have came in contact with live fencing wire, got electric shock and met with the fatal electrical accident. | AWAITED | NA | NA | NA | Godhra
47 | BUFFALO of Ratanbhai Mohanbhai Baria, RAJPARI PATEL FALIYA, Vill-Rajpari, Tal-Bodeli, Dist-Vadodara |  |  | 2022-08-18 | FA |  |  | DUE TO HEAVY RAIN & WIND SEASON THE SERVICE WIRE OF ANGANWADI CONNECTION TOUCH TO THE GI EARTHIMG WIRE OF PSC POLE .THE LEAKAGE CURRENT PASS THROGH GI EARTHING WIRE AND BUFFALO CAME IN CONTACT WITH EARTHING WIRE AND GOT ELECTROCUTED.SO BUFFALO DIED AND EL | Awaited | NA | NA | Service Replaced and Rejumper | Baroda O&M
48 | HATHILA NARSINGBHAI SAMSUBHAI'S BULLOCK, Vill-KHAREDI, Tal/Dist-Dahod |  |  | 2022-08-19 | FA |  |  | BULLOCK WAS WONDERING NEAR TC CENTRE. TC CENTRE AND LAND WAS WET DUR=E TO RAIN, BULLOCK MAY CAME IN CONTACT WITH WET TC RSJ POLE AND ELECTROCUTED | AWAITED | NA | NA | TC AND LINE MAINT. IS CARRIED OUT. | Godhra
49 | Parsingbhai Hakjibhai Pargi, tribhuvan welding work tergola faliya, Vill-kaliya valunda, Tal-fatepura, Dist-Dahod |  |  | 2022-08-22 | FHO-Pvt |  |  | On Dt. 22.08.2022, Fatal Accident occured to victim Shri Parsingbhai Hakjibhai Pargi in consumer private premise in the name of Shri Bhuriben Badjibhai Damor having Consumer No- 19046022200, On the same day i.e. 22.08.22 site was visited and it was found | AWAITED | NA | NA | NA | Godhra
50 | MUKESHBHAI GOKADBHAI BARIYA, PATEL FADIYU VILL-MOJARI, TAL-MORVA (HADAP), Dist-Panchmahal |  |  | 2022-08-23 | FHO |  |  | LT CONDUCTOR SNAPPED DUE TO HEAVY RAIN | AWAITED |  |  | LT line maintenance carried out | Godhra
51 | Buffalo of Rameshbhai Dhulabhai Machhi, Mandir Faliyu, Vavor Road, Vill-Juna Vallavpur, Tal-Shahera, Dist-Panchmahal |  |  | 2022-08-24 | FA |  |  | Neem Tree Branch fell on Lt line resulting in snapping of neutral LT Conductor (2 Wire Open line) due to rain and wind around 05:15 am on the road (as per witness). Meanwhile the buffalo went for grazing and came in contact with this wire got electrocuted | AWAITED | NA | NA | BARE CONDUCTOR REPLACE BY ABC CONDUCTOR | Godhra
52 | MAHESHKUMAR AMARSINH SOLANKI, APRUJI MOTA FALIYA, Vill-Apruji, Tal-Kathlal, Dist-Kheda |  |  | 2022-08-25 | FA |  |  | DUE TO RAIN,SHE BUFFALO PASSING NEAR 25 KVA TRANSFORMER LOCATION NO-94/12,SHE CAME IN CONTACT WITH GI EARTHING WIRE OF THIS TRANSFORMER,AND GOT ELETRODUCED AND FATAL ANIMAL ACCIDENT OCCURED | AWAITED | NA | NA | Earthing of Transformer Done | Nadiad
53 | BULLOCK owner: RATHWA SABURBHAI SURSINGBHAI, Vill-JALARIYA, Tal-Halol, Dist-Panchmahal |  |  | 2022-08-25 | FA |  |  | THE TOP CONDUCTOR JUMPER TOUCHED TO AN ANGLE AND EARTH WIRE BECOME LIVE | AWAITED | NA | NA | JUMPER REPLACED & RECTIFICTION DONE | Godhra
54 | BULL-Rathava Shankarbhai Sengalabhai, Vill-KHODAVANIYA (Mal Faliyu), Tal/Dist-Chhotaudepur |  |  | 2022-08-25 | FA |  |  | The accident occured due to LT Line Live conductor snapped and fall"s on bull which was passing below LT Line.unfortunately bull come in contact with live conductor and got electocuted. | Awaited | NA | NA | Conductor rejoint and stringing | Baroda O&M
55 | Buffalo OWNER-BHARATSINH MANSINH SOLANKI, Vill-KANKODAKOI, Tal-Ghoghamba, Dist-Panchmahal |  |  | 2022-08-25 | FA |  |  | FATAL ANIMAL BUFFALO ACCIDENT OCCURED ON 25-08-2022 DUE TO 2W OPEN LT ONE CONDUCTOR SNAPPED IN FIELD AND THAT TIME BUFFALO GRAZING GRASS AND CONTACT WITH LIVE WIRE SO BUFFALO ELECTROCUTED IN FARM | AWAITED | NA | NA | LT MAINTANANCE CARRIED OUT & CONDUCTORE REPLACED | Godhra
56 | Hasmukhbhai Dineshbhai Parmar, Vill-Khanpur (Manchha Vistar), Tal/Dist-Anand |  |  | 2022-08-29 | FHO |  |  | Voctim was doing labour work of loading of Banana looms from farm to truck and he was on the cabin of truck and might be touch the 11 kv line and met fatal accident. | Awaited | NA | NA | No action required | Anand
57 | 1)SHRI JITENDRABHAI GORDHANBHAI TALPADA, (2)RAJUBHAI DALSUKHBHAI PALAS, NEAR GITA PARK SOCIETY,GITANJALI CHOKDI,PIJ ROAD,NADIAD. |  |  | 2022-08-31 | FHO |  |  | SHRI JITENDRABHAI GORDHANBHAI TALPADA AND SHRI RAJUBHAI DALSUKHBHAI PALAS WERE DOING MANDAP TADPATRI WORK ON STEEL STRUCTURE UNDER O/H H.T LINE AND SUDDENLY HIS HEAD TOUCHED TO LIVE CONDUCTOR AND BOTH VICTIMS GOT ELECTROCUTED AND DIED | AWAITED | NA | NA | Safty awareness programme being arranged among consumers for safty awareness. | Nadiad
58 | Bhoi Dilipbhai Rayjibhai, Pathra Faliyu(Sim Vistar), Vill-Ujada, Tal-Shahera, Dist-Panchmahal |  |  | 2022-09-07 | FHO |  |  | Bavad Tree Branch (Acacia Tree) Fell On The 2W Open LT Line Due To Heavy Wind Resulting In Snapping Of One Wire Which Fell On Ground. Meanwhile It Was Informed By Locals That In Morning Around 06:30 AM Victim (Dilipbhai Rayjibhai Bhoi) Went In The Field T | AWAITED | NA | NA | BARE CONDUCTOR REPLACED BY 2 W ABC | Godhra
59 | COW OF BABUBHAI HEMJIBHAI RABARI, Vill-Mandala, Tal-Dabhoi, Dist-Vadodara |  |  | 2022-09-07 | FA |  |  | LT CONDUCTOR OF SHRI VINUBHAI VITTHALBHAI PATEL'S AG CONNECTION WAS BROKEN DUE TO HEAVY RAIN AND WIND,WHEN COW CAME IN CONTACT WITH BROKEN LT CONDUCTOR & COW GOT ELECTROCUTED & BECAME FATAL. | Awaited | NA | NA | providing LT AB cable with extension. | Baroda O&M
60 | 1)SUNIL NAGINBHAI VASAVA 2)KANU CHANDU VASAVA, B/W PISAI MANDALA ROAD, Vill-Mandala, Tal-Dabhoi, Dist-Vadodara |  |  | 2022-09-08 | FHO |  |  | VICTIM HAS PARKED HIS TURCK UNDER HT LINE WHILE KANUBHAI WAS SITTING ON TRUCK'S CABIN WHILE TURNING THE TRUCK,VICTIM KANUBHAI STOOD UP FROM THE TRUCK AND VICTIM KANUBHAI WAS ELECTROCUTED MAYBE BY COME IN CONTACT WITH LIVE CONDUCTOR OF HT LINE OF PISAI JG | Awaited | NA | NA | RESTRINGING OF CONDUCTOR & PROVIDED OF HT EXTENSION | Baroda O&M
61 | SODHA PARMAR BHUPATSINH ANDARSINH, BAJAKPURA SIM VISTAR, Tal-Kathlal, Dist-Kheda |  |  | 2022-09-08 | FHO |  |  | DUE TO HEAVY WIND AND RAIN CONDUCTOR OF 11 KV SHAHPUR AG FEEDER BROKEN DUE TO GULMOHAR TREE BRANCH FALLEN ON IT AND VICTIM ACCIDENTALLY COMES IN CONTACT WITH THIS BROKEN CONDUCTOR AND DIED ON THE SPOT | AWAITED | NA | NA | CONDUCTOR JOINTED AND TWO NOS OF PSC POLE | Nadiad
62 | MEHULBHAI SHRAVANBHAI TALAPDA, NEAR BHARWAD VAS, Vill-Kharenti, Tal-Matar. Dist-Kheda |  |  | 2022-09-08 | NFHO |  |  | Victim was going for any work and pass near LT pole in bharwad vas. During this time Victim accidently touched with hangging stay wire and got electric shock and fell down on the earth | AWAITED | NA | NA | FOR SAFETY PURPOSE POWER SUPPLY MADE OFF | Nadiad
63 | BARIA BHIMSINGBHAI LAKHABHAI, Near meter board Baman Faliya Vill-Kanjipani, Tal-Jambughoda, Dist-Panchmahal |  |  | 2022-09-10 | FHO-Pvt |  |  | DUE TO DAMAGED IN WIRING THE METAL BODY SWITCH WAS ELECTROCUTED AND VICTIM WAS MAKING SWITCH ON FOR IRRIGATION | AWAITED | NA | NA | NA | Godhra
64 | Cow of Paaniben Manilaal Mayavanshi, Vankar Faliyu, Vill-Kambopa, Tal-Balasinor, Dist-Mahisagar |  |  | 2022-09-10 | FA |  |  | Tree Branch fallen due to heavy rain and wind on the two wire LTLine ,Cow was tied under line ,broken cond touched with back side leg of the cow and cow died due to electric shock. | AWAITED | NA | NA | broken conductor jointed | Nadiad
65 | OX OWNER - VIKRAMBHAI BALSINGBHAI RATHWA, VALOTHI VILLAGE - SMASHAAN FALIYA, Tal-Bodeli, Dist-Chhotaudepur |  |  | 2022-09-11 | FA |  |  | ON DT. 11.09.2022 ONE OF THE OX OF SH. VIKRAMBHAI BALSINGBHAI RATHWA WAS PASSING ON THE KACHHA ROAD NR. SMASHAAN OF VALOTHI VILLAGE AND ACCIDENTALLY STEPPED ON THE LIVE LT LINE CONDUCTOR FALLEN ON GROUND (DUE TO LT PSC POLE WAS BROKEN BY FALLING OF TREE O | Awaited | NA | NA | Conductor rejoint and stringing | Baroda O&M
66 | buffalo of BHARVAD SAVABHAI AALABHAI, VERAI MATA FALIYU, Vill-Juni Koshial, Tal-Matar, Dist-Kheda |  |  | 2022-09-11 | FA |  |  | At that Accident place buffalo eating grass near transformer centre. During at time suddenly fell down on the earth and died on the spot. No any exact reason for this incident. | AWAITED | NA | NA | MAINTENANCE DONE | Nadiad
67 | Prabhubhai chikabhai ranghadiya Chuahan (LM), malawada chokdi area, Vill-Limbasi, Tal-Matar, Dist-kheda |  |  | 2022-09-12 | NFHD |  |  | During LT complain work victim was climbed on 11kv Pariej jgy ht pole for replace the break service line with GI wire of shri patel parbatbhai devjibhai at malawada chokdi. During this work GI wire of service line accidently touched with 11kv line conduct | AWAITED | NA | NA | it is instruced line staff to wear safety article. | Nadiad
68 | MOYYUDIN KAIYUMBHAI LUHAR, AHMEDABAD INDORE HIGH WAY,SMASHAN ROAD.OPP DARGAH, Vill-Raliyati, Tal/Dist-Dahod |  |  | 2022-09-12 | FHO |  |  | As per information received at site Mr Shahrukh Shabbirbhai Bajariya and Mr. Moyyudin Kaiyumbhai Luhar were working on installing a banner with metalic frame on the terrace of the shop.11 Kv Sahkarnagar feeder was passing nearby his shop and a 16 KVA tran | Awaited | NA | NA | Notice issued regarding illegal construction vide 3886/12.09.2022 | Godhra
69 | Mr. Shahrukhbhai Shabbirbhai Bajariya, AHMEDABAD INDORE HIGH WAY,SMASHAN ROAD.OPP DARGAH, Vill-Raliyati, Tal/Dist-Dahod |  |  | 2022-09-12 | NFHO |  |  | As per information received at site Mr Shahrukh Shabbirbhai Bajariya and Mr. Moyyudin Kaiyumbhai Luhar were working on installing a banner with metalic frame on the terrace of the shop.11 Kv Sahkarnagar feeder was passing nearby his shop and a 16 KVA tra | Awaited | NA | NA | Notice issued regarding illegal construction vide 3886/12.09.2022 | Godhra
70 | MADHUBHAI SOMABHAI'S COW, KABIR FALIYA VILLAGE TC, Vill-Sura Sultanpura, Tal-Halol, Dist-Panchmahal |  |  | 2022-09-12 | FA |  |  | As per site visit it is found that there is no leakage current at the time of site visit but it may be possibility of leakage current pass through tarnsformer earthing wire and at that time cow was touching with earthing wire and get electrocuted and died | AWAITED | NA | NA | TC EARTHING REACTIVATED ,NECESSARY MAINTENACE WORK DONE | Godhra
71 | mahendrabhai isharbhai patel, nr segva shre transport petrol pump, Vill-Segva, Tal-Sinor, Dist-Vadodara |  |  | 2022-09-13 | FA |  |  | due to heavy rain 7 wind conductor collied with eachother & due to that lt conductor snapped & while grassing shee buffalo came in contact with & electorcuted & died. | Awaited | NA | NA | REBINDING OF CONDUCTOR & RESTRING OF LT LINE | Baroda O&M
72 | Buffalo of Bharvad Gordhanbhai Amrabhai, Beh Vinayaka Institute, Nr Shiv Tirth Vadtal Road, Bakrol, Tal-Dist-Anand |  |  | 2022-09-14 | FA |  |  | Animal (young buffalo) came in touch with snapped LT Line conductor (AG LT) | Awaited | NA | NA | Restringing done after rectification. | Anand
73 | SAVITABEN NATWARBHAI DINDOR, Vill-BHANDARA, Tal-Santrampur, Dist-Mahisagar |  |  | 2022-09-17 | FHO-Pvt |  |  | WHILE CROSSING THE FARM SHE ACCIDENTLY CAME IN CONTACT WITH THE FENCING WHICH WAS MADE TO PREVENT TO UNNECCERY ANIMALS ENTIRING IN TO THE FARM THE FENCING MAY HAD ELECTRICAL SUPPLY GIVEN THROUGH UN AUTHORISED PRIVATE WIRE SHE ACCIDENTLY CAME IN CONTACT WI | AWAITED | NA | NA | NA | Godhra
74 | BUFFALO (OWNER NAME-SOLANKI ARJANBHAI UDABHAI), MIRAPURA(NEAR LEADY TALAVADI), Tal-Kapadvanj, Dist-Kheda |  |  | 2022-09-23 | FA |  |  | On date:-23.09.2022 around 6:00 PM at vill-Mirapura (Nr-Leady Talavadi)when an animal she buffalo was drinking water at leady Talavadi after passing near 10 KVA Transformer of 11 KV Sorana Jgy feeder , Location no-SRN/TC NO/063 for graze, She buffalo fo | AWAITED | NA | NA | MAINTENANCE OF TC STRUCTURE CARRIED OUT | Nadiad
75 | Jayesh Bhunda Bhil, At the farm of vinod trikam patel , Vill-Kandevar, Tal-Sankheda, Dist, Chhotaudepur |  |  | 2022-09-29 | FHO |  |  | Victim was spray pestisized with the help of tractor attached tenkar of petisized on cotton crop of vinod trikam patel farm while compliting work when they passes under 11 kv line by mistake wiper of spray tanker touch with 11 kv line and got accedent | Awaited | NA | NA | No action required | Baroda O&M
76 | Sagarbhai Sevaliya Bhil, At the farm of vinod trikam patel , Vill-Kandevar, Tal-Sankheda, Dist, Chhotaudepur |  |  | 2022-09-29 | NFHO |  |  | Victim was spray pestisized with the help of tractor attached tenkar of petisized on cotton crop of vinod trikam patel farm while compliting work when they passes under 11 kv line by mistake wiper of spray tanker touch with 11 kv line and got accedent | Awaited | NA | NA | No action required | Baroda O&M

## SOP-03
Name of Distribution Licensee: M G V C L
Quarter : Q-II (Jul-Aug-sept- 2022)
Year: 2022-23
REGISTER FOR COMPILING THE COMPLAINTS CLASSIFICATIONWISE Q-I 2022-23
Performa SoP 003 B: |  |  |  | APPENDIX-B (already in the SoP regulation)
Classification | Nature of Complaints | Pending complaints of previous qtr. | Complaints received during the qtr. | Total Complaints =2+3 | No. of Complaints redressed during the quarter. |  |  |  |  | Balance Complaints to be redressed. (4) – (9)
[5 empty] | In stipulated time |  | Beyond stipulated time |  | Total (5) to (8)
[5 empty] | Within 50% of stipulated time. | Within stipulated time. | Up to double the stipulated time | More than double the stipulated time
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
A(i) | Loose Connection | 0 | 87899.6426 | 87899.6426 | 38605.9551 | 49293.6874 | 0 | 0 | 87899.6426 | 0
A(ii) | Intruption due to line Break down | 0 | 63774.5109 | 63774.5109 | 24656.8173 | 39117.6936 | 0 | 0 | 63774.5109 | 0
A(iii) | Intruption due to T/C Fail | 0 | 5674.3128 | 5674.3128 | 2678.2346 | 2996.0782 | 0 | 0 | 5674.3128 | 0
B(i) | Quality of power supply,ordinary case which require no Augmentation | 0 | 8610.6585 | 8610.6585 | 5357.1792 | 3253.4792 | 0 | 0 | 8610.6585 | 0
B(ii) | Quality of power supply,ordinary case which require Augmentation | 0 | 5398.7795 | 5398.7795 | 3180.7883 | 2217.9912 | 0 | 0 | 5398.7795 | 0
C(i) | Meters- Stoped/Defective meter | 0 | 16280.9295 | 16280.9295 | 9593.4654 | 6687.4641 | 0 | 0 | 16280.9295 | 0
C(ii) | Meters- Billing on average basis for > two bills | 0 | 6841.2473 | 6841.2473 | 3938.4074 | 2902.8399 | 0 | 0 | 6841.2473 | 0
D(i) | Over head lines - loose wires | 0 | 6649.1212 | 6649.1212 | 3433.9055 | 3215.2157 | 0 | 0 | 6649.1212 | 0
D(ii) | Over head lines - in adiquate ground clearance | 0 | 2257.1236 | 2257.1236 | 1524.5183 | 732.6053 | 0 | 0 | 2257.1236 | 0
E(i) | Bills- for current bills where no addl information required | 0 | 6201.7593 | 6201.7593 | 3902.2316 | 2299.5276 | 0 | 0 | 6201.7593 | 0
E(ii) | Bills- for current bills where addl information required | 0 | 3611.5234 | 3611.5234 | 1902.9572 | 1708.5662 | 0 | 0 | 3611.5234 | 0
F(i) | Service connections- where extention of mains is not required | 0 | 16932.9321 | 16932.9321 | 8314.3747 | 8618.5574 | 0 | 0 | 16932.9321 | 0
F(ii) | Service connections- where extention of mains is required | 0 | 5685.9446 | 5685.9446 | 3339.9877 | 2345.9569 | 0 | 0 | 5685.9446 | 0
F(iii) | Service connections- Modification in connected load | 0 | 5082.0013 | 5082.0013 | 1486.8351 | 3595.1662 | 0 | 0 | 5082.0013 | 0
F(iv) | Service connections- Name change/reconnection | 0 | 3900.3923 | 3900.3923 | 1899.9332 | 2000.459 | 0 | 0 | 3900.3923 | 0
G | Refund of amount due inregard to temp conn | 0 | 638.2686 | 638.2686 | 396.688 | 241.5806 | 0 | 0 | 638.2686 | 0
H | Others | 0 | 26226.8526 | 26226.8526 | 13438.5298 | 12788.3229 | 0 | 0 | 26226.8526 | 0
| TOTAL | 0 | 271666 | 271666 | 127650.8084 | 144015.1916 | 0 | 0 | 271666 | 0
The format is to be sent quarterly
The quarterly reporting of the year means reporting for the period 1st Quarter as Jan – Mar, 2nd Quarter as Apr – Jun, 3rd Quarter as Jul – Sep and 4th Quarter as Oct – Dec of the year.
For any other complaints not mentioned in the classification, the sequence for (H) can be used.

## SOP-04
Name of Distribution Licensee: M G V C L
Quarter : Q-II (Jul-Aug-sept- 2022)
Year: 2022-23
Performa SoP 004 : Publicity carried out while displaying the contact details of consumer complaints centers
Particulars should also cover the details of consumer awareness program conducted, advertisement done through various media like TV, newspaper, radio, pamphlets & booklet distributions, Displays etc. The development of website and any medium through which public education is carried out can be included.
Sr. No | Actions or steps carried out by distribution licensee towards public awareness in the quarter | Likely number of consumers influenced
1 | RTI Officers Name is displayed at customer care centre on each office | 3439096
2 | Necessary information regarding time schedule for new connection and solving complaints is display on the board. | 3439096
3 | Contact nos. of various officers of the company for emergency contact is also displayed at customer care centre. | 3439096
4 | Displayed safety posters at various S/dn,Divisions | 4080
5 | Safety Meeting with Line Staff at various S/dn,Divisions on Every Monday (Line staff influenced) | 14000

## SOP-05
Name of Distribution Licensee: M G V C L
SOP Q-II (July-Aug-Sept-22)
Year :2022-23
Performa – SoP 005 B: Action taken report by the Redressal Committee
Sr. No | Month | Date and Time Meeting conducted | No of complaints registered at the meeting | No. of complaints pending at the end of the meeting
1 | 1st Month of the quarter (July'22) | 28.07.22,11.30 am at Corporate Office | 3 | 1
2 | 2nd Month of the quarter (Aug'22) | 26.08.22,11.30 am at Corporate Office | 5 | 0
3 | 3rd Month of the quarter (Sept'22) | Nil | 0 | 0

## SoP - 06
Name of Distribution Licensee: M G V C L
Financial Year: 2022-23
Quarter : Q-II (Jul-Aug-Sep-2022 )
Performa SoP 006: Failure of Distribution Transformer
Sr. No. | Name of Circle | Nos. of existing Distribution Transformers at the start of the quarter | Nos. of Distribution Transformers added during the quarter | Total number of Distribution Transformers on end of quarter | Total number of Distribution transformer failed during quarter-II | % failure rate of Distribution transformer
|  | A | B | C=A+B | D | H = (D)*100/C
1 | Baroda O&M | 52465 | 717 | 53182 | 932 | 1.7525
2 | Baroda City | 9088 | 103 | 9191 | 30 | 0.32641
3 | Anand | 24429 | 25 | 24454 | 396 | 1.6194
4 | Nadiad | 32342 | -1168 | 31174 | 494 | 1.5847
5 | Godhra | 58571 | 1016 | 59587 | 1052 | 1.7655
| MGVCL | 176895 | 693 | 177588 | 2904 | 1.6352

## SoP008
Name of Distribution Licensee: M G V C L
Quarter : Q-2 (July-Aug-Sep- 2022)
Year: 2022-23
Performa SoP 008: Sample Test result for Neutral Voltage
Compliance Sample Test Report for Neutral Voltage
-1 | -2 | -3 | -4 | -5 | -6
Sr. No | Category of consumers | Sample Size | Standard specified in regulation | Deviation of results from the sample test (Numbers) | % age compliance
|  | (Numbers) |  |  | (6) = (5)*100/(3)
| LT consumers | 1441 | 2% | 0 | 0
1 | Domestic | 1023 | 2% | 0 | 0
2 | Commercial | 242 | 2% | 0 | 0
3 | Industrial | 23 | 2% | 0 | 0
4 | Agricultural | 143 | 2% | 0 | 0
5 | Public water works | 10 | 2% | 0 | 0
| HT consumers |  | 2%
6 | HT industrial | 5 | 2% | 0 | 0

## SoP009
Name of Distribution Licensee: M G V C L
Quarter : Q-2 (July-Aug-Sep- 2022)
Year: 2022-23
Performa SoP 009: Sample Test result for Voltage variations
Compliance Sample Test Report for voltage variations
-1 | -2 | -3 | -4 | -5
Voltage Level | Sample Size (numbers) | Limit or prescribed standard | Deviation of results from the sample test (Numbers) | % age compliance
(5) = (4)*100/(2)
Low Voltage | 56 | +6% to -6% | 0 | 0
High Voltage | 24 | +6% to -9% | 0 | 0
Extra High Voltage | 1 | +10% to -12.50% | 0 | 0

## SoP010
Name of Distribution Licensee: M G V C L
Quarter : Q-2 (July-Aug-Sep- 2022)
Year: 2022-23
Performa SoP 010: Sample Test result for Harmonics
Compliance Sample Test Report for Harmonics
-1 | -2 | -3 | -4 | -5 | -6
Sr. No | Category of consumers | Sample size (Numbers) | Limit or standard prescribed | Deviation of results from the sample test (Numbers) | %age compliance
(6) = (5)*100/(3)
1 | LT consumers | 33 | 3.5% | 0 | 0
2 | HT consumers | 4 | 3% | 0 | 0
3 | EHT consumers | 1 | 3% | 0 | 0
Note: The licensee shall also submit along with the above harmonic data, the records of customer wise drawls of harmonic currents measured at various strategic points.
The formats SoP 008, SoP 009 and SoP 010 have to be sent annually.
For the purpose of annual submissions, the year end has to be considered as the end of December month of a particular year.

## SOP 11A
Name of Distribution Licensee: M G V C L
QuarterII (July-22 to Sept-22)
Year:2022-23
SoP 011 –A: System Average Interruption Frequency Index (SAIFI)
Sr. No | Month | Ni - Total no of customers for each momentary interruptions | NT - Total no of customers served |  |  | Past year corrosponding Month
1 | 2 | 3 | 4 | 5 | 6=5/4 | 7
1 | July' 22 | 3213838 | 3430171 | 20251974 | 5.9041 | 5.0998
2 | Aug' 22 | 3165235 | 3439978 | 15118870 | 4.395 | 3.8415
3 | Sept' 22 | 3190435 | 3439096 | 15761266 | 4.583 | 6.4162
|  |  | 10309245 | 51132110 | 4.9598 | 5.1205

## SOP-11B
Name of Distribution Licensee: M G V C L
QuarterII (July-22 to Sept-22)
Year:2022-23
SoP 011 – B System Average Interruption Duration Index (SAIDI)
Sr. No | Month | ri = Restoration Time for each interruption event | Ni - no of interrupted customers for each sustained interruption event | ri * Ni – Total customer interruption Duration | ri=Restoration Time for each interruption event | Ni= No of Interrupted customers for each sustained Interruption | NT - Total no of customers served | Customer Interruption Duration |  |  | Past year corrosponding Months
[9 empty] | MINS. | HRS. | MINS. | HRS.
1 | 2 | 3 | 4 | 5= 3 X 4 | 3 | 4 | 5 | 6 | 7=4/3 | 7A | 8 | 8A
1 | July' 22 | July |  |  | 1001351 | 3213838 | 3430171 | 1204297477 | 351.0896 | 0.24375 | 331.9894 | 0.23056
2 | Aug' 22 | August |  |  | 703634 | 3165235 | 3439978 | 870579789 | 253.0771 | 0.17569 | 260.7251 | 0.18125
3 | Sept' 22 |  |  |  | 835068 | 3190435 | 3439096 | 1116527662 | 324.6573 | 0.22569 | 389.7374 | 0.27083
[6 empty] | 9569508 | 10309245 | 3191404928 | 309.5673 | 0.21528 | 327.5597 | 0.22778

## SOP-11C
Name of Distribution Licensee: M G V C L
QuarterII (July-22 to Sept-22)
Year:2022-23
SoP 011 – C: Momentary Average Interruption Frequency Index (MAIFI)
Sr. No | Month | Number of Momentary interruptions Imi | Nmi - Total no of customers for each momentary interruptions | NT - Total no of customers served |  |  | Past year corrosponding Month
1 | 2 | 3 | 4 | 5 | 6 | 7=6/5 | 8
1 | July' 22 | 25703 | 3073031 | 3430171 | 42119366 | 12.2791 | 12.0225
2 | Aug' 22 | 23328 | 3017134 | 3439978 | 38075153 | 11.0684 | 10.0084
3 | Sept' 22 | 22039 | 2956486 | 3439096 | 35248428 | 10.2493 | 12.7904
|  |  |  | 10309245 | 115442947 | 11.198 | 11.6093

## SoP - 13
Name of Distribution Licensee: M G V C L
Financial Year: 2022-23
Quarter : Q-II (Jul-Aug-Sep-2022 )
Performa SoP 013: Faulty Meters Replacement
Consumer Category | No. of faulty meters at the start of the quarter | No. of faulty meters added during the quarter | Total no. of defective / faulty Meter | No. of faulty Meters repaired and replaced | No of faulty meters pending at the end of the quarter | Remark
| 1 | 2 | (3)=(2)+(1) | 4 | (5)=(3)-(4)
1 PHASE
MGVCL | 6469 | 26933 | 33402 | 26150 | 7252
3 PHASE
MGVCL | 1620 | 3411 | 5031 | 4421 | 610

## SoP_15
Performa SoP 015: Release of New Connection status for FY 2022-23
Qtr | Consumer category | Total no. of consumers connected at the beginning of half-year/year | Pending at the Beginning of the of the Half year/year | New Applications received during the half-year / year | No. of connections released during the half-year / year | No. of applications pending at the end of half-year / year | Total no. of consumers connected at the end of half-year/year
1st Half (Apr-May-Jun-Jul-Aug-Sep) | Domestic | 2789509 | 1052 | 37407 | 29450 | 1122 | 2818959
| Commercial (NRGP_C+LTMD_C) | 316385 | 367 | 8706 | 8144 | 233 | 324529
| Industrial LT (NRGP_L+LTMD_L) | 39054 | 161 | 876 | 728 | 15 | 39782
| Agriculture (Total) | 180842 | 10533 | 4806 | 6473 | 8775 | 187315
| Industrial HT | 2699 | 58 | 115 | 123 | 26 | 2822
| Total | 3328489 | 12171 | 51910 | 44918 | 10171 | 3373407

## SoP 16
Name of Distribution Licensee: M G V C L
Quarter : Q-2 (July-Aug-Sep- 2022)
Year: 2022-23
Performa SoP 016: Compensation details
COMPENSATION DETAILS
Sr.No. | Event | Compensation | No of cases where compensation was given (in numbers) | Amt of compensation paid (in Rs.)
1 | Duty to provide supply | Rs. 50 per day of delay from the limit specified in the performance regulations | 0 | 0
| a) New Connection |  | 0 | 0
| b) Additional Load |  | 0 | 0
| c) Temporary supply |  | 0 | 0
| d) Shifting service connection |  | 0 | 0
| e)Transfer of service connection |  | 0 | 0
| f) Change in tariff category of consumer |  | 0 | 0
2 | Complaints in billing | Rs. 50 for non reply within the period prescribed in Regulations | 0 | 0
3 | Replacement of meters | LT- Rs. 25 per day of delay - maximum Rs.2,500 and HT - Rs. 250 per day of delay - maximum of Rs.5,000 | 0 | 0
4 | Interruption of supply | LT- Rs. 25 for every 6 hrs of delay- maximum of Rs. 500 and HT- Rs. 50 for every 6 hrs delay- maximum Rs. 1000/- | 0 | 0
5 | Voltage fluctuations and complaints | Rs. 50 for failure to visit or convey findings within the stipulated period | 0 | 0
6 | Responding to consumer's complaints | Rs. 25 for each day of delay- maximum Rs. 500 | 0 | 0
7 | Grievance Handling | Rs.25 for failure in handling grievance | 0 | 0
TOTAL |  |  | 0 | 0