## MG COVER PAGE
Name of Distribution Licensee: M G V C L
Quarter : Q-III (Oct-Nov-Dec- 2022)
Year: 2022-23

## MG SoP 01
Name of Distribution Licensee: M G V C L
Quarter III (OCT-22 to DEC-22)
Year:2022-23
Performa - SoP 001: Fatal and Non-Fatal electrical accident report
NUMBER OF ACCIDENTS FOR THE 3rd QUARTER OF 2022-23
Sr.No | Name of Area/Circle | No of accidents in the quarter |  |  |  |  | Cumulative since the first quarter of the current FY 2020-21 |  |  | Cumulative since the first quarter of the Last FY 2021-22
|  | Departmental |  | Outside |  |  | TOTAL |  |  | TOTAL
|  | FH | NFH | FH | FA | NFH | FH | FA | NFH | FH | FA | NFH
1 | Baroda (City) | 0 | 2 | 0 | 0 | 0 | 1 | 0 | 2 | 1 | 4 | 1
2 | Baroda (O&M) | 0 | 4 | 2 | 4 | 0 | 8 (1-Pvt) | 19 | 11 | 8 | 26 | 8
3 | Anand | 0 | 1 | 0 | 1 | 0 | 2 | 4 | 2 | 7 | 11 | 3
4 | Godhra | 0 | 1 | 1 | 3 | 3 | 16 (9-Pvt) | 24 (2-Pvt) | 8 | 10 (1-Pvt) | 35 | 5 (1-Pvt)
5 | Nadiad | 0 | 0 | 1 | 3 | 0 | 9 (2-Pvt) | 22 | 8 | 7 | 17 | 3
| TOTAL | 0 | 8 | 4 | 11 | 3 | 36 (12-Pvt) | 69 (2-Pvt) | 31 | 33 (1-Pvt) | 93 | 20 (1-Pvt)
FH – Fatal Human, FA – Fatal Animal, NFH – Non-fatal Human | [5 empty] | 26 |  |  | 136 |  |  | 146
PVT - Private Premises Accident.

## MG SOP2
Performa – SoP 003: Action taken report for safety measures complied for the electrical accidents occurred
ACTION TAKEN REPORT FOR SAFETY MEASURES COMPLIED FOR THE ELECTRICAL ACCIDENTS OCCURED IN THE Third QUARTER OF FY 2022-23
1 | 2 |  |  | 3 | 4 |  |  | 5 | 6 | 7 | 8 | 9 | 10
Sr. No | Location of Accident and details of the victim | Address | sdn | Date of occurrence | Type of Accident | Installation | Accident Type | Cause of Accident | Findings of CEI / EI / AEI | Remedies suggested by CEI /EI / AEI in various cases | Whether the remedy suggested is complied | Action taken to avoid recurrence of such Accident | Circle office
1 | Bhavinbhai Matabhai Meda, Sharda Meda faliya, Tal-Zalod, Dist-Dahod |  |  | 2022-10-01 | NFHO |  |  | As per the information rceived from Sarpanc Shri GP at.Sharda meda faliya,The accident was occur.As per statement of eye witness victim was passing at location,the victim was thrown away.At the time of side visit NO Direct Leakage current found on the X | AWAITED | NA | NA | HT AND TC MAINTENANCE CARRIED OUT | No
2 | SUNIL RAMDAYAL SUTHAR, Premises of Lakhraj Dharamsinh Gor, Vill/Taluka-Dabhoi, Dist-Vadodara |  |  | 2022-10-02 | FHO |  |  | Victim was fitting the elevation aluminium board frame by screw to iron shade by standing on woolen palk.accidently victim loss his balance and victim’s left hand may came contact with live open conductor of 11kv dabhoi town feeder, he was fall down and | Awaited | NA | NA | No action required | NO
3 | Sh. Hathibhai Sardarbhai Khant, RAVNA FALIYA, Vill-Kamrol, Tal-Waghodia, Dist-Vadodara |  |  | 2022-10-03 | FHO |  |  | Sh. Hathibhai Sardarbhai Khant was working as conductor on vehicle on GJ01 ET1549 dumper truck. Near Ravna faliya of village kamrol driver parked the under 11KV line of kotambi AG feeder and raised the trolley to unload querry metal in road side in this p | Awaited | NA | NA | No action required | NO
4 | Bull of RATHAVA AMBUBHAI DHANIYABHAI, SAYADA FALIYU, Vill-Bhilpur, Tal/Dist-Chhotaudepur |  |  | 2022-10-04 | FA |  |  | The accident occured due to cyclone & heavy wind come at village bhilpur (Sayada Faliyu) due to which 03 nos of HT pole & 01 nos TC structure of HT tap line of 11 KV Siloj AG feeder broken with live conductors & fall down on ground.Live conductors snapped | Awaited | NA | NA | RCTIFICATION WORK DONE | NO
5 | Buffalo of Bharvad Anilkumar Ramubhai, Lunawada,near kanka TALAV, Tal-Lunawada, Dist-Mahisagar |  |  | 2022-10-05 | FA |  |  | LT 2 wire abc touch with gaurding and damage abc 2wire and puncture . due to this situation current pass though gaurding wire to psc pole earthing wire and earthing wire also damged to bottom ground leveal and touch with iron fancing and accident occure3d | AWAITED | NA | NA | GUARDING REMOVED ,EARTHING RE ACTIVATION DONE | No
6 | SHE BUFFALO of Ramabhai V Zala, Vill-DHULIYA VASNA, Tal-Kapadwanj, Dist-Kheda |  |  | 2022-10-07 | FA |  |  | DUETO HEAVY RAINING BIG TREE BRANCH FALLEN ON LT LINE OF KRISHNA JGY FEEDER TC NO:12 LT LINE,BECAUSE OF THAT NE CONDUCTORE SNAPPED AND FALLEN ON GOUND.DURING GRAZING SHE BUFFAO CAME IN CONTACT WITH BROKEN LT OPEN CONDUCTOR AND ELECTUDE AND ACCIDENT OCCURE | Tree branch fallen on LT Line | Electric asset to be maintained regularly for safty purpose. | yes | Maintenace was carried out. | Yes
7 | ASHWINBHAI NARANBHAI RATHWA, NEAR THE TEMPLE OF PANDHRA VILLAGE, Tal-Bodeli, Dist-Chhotaudepur |  |  | 2022-10-07 | NFHD |  |  | JUMPER OF 11KV SURYA JGY DODP AT VILLAGE PANDHRA WAS BURNT.SO VICTIM WAS REPARING THE JUMPER ON DODP.POWER WAS CUT OFF BY REMOVING THE DO OF DODP AT VILLAGE VISADI AND EARTHING WAS ALSO DONE BY VICTIM.SOMEHOW POWER WAS COME TO DODP AND VICTIM WAS GET ELEC | Awaited | NA | NA | REJUMPERING WORK DONE AND ALL LINE STAFF WERE INSTRUCTED DO EARTHING ON BOTH SIDE AND SHORT ALL 3 CONDUCTOR | NO
8 | Govind K Katara, Navinagari pachhal, Vill-Patod, Tal-Padra, Dist-Vadodara |  |  | 2022-10-08 | NFHD |  |  | Under the supervision of Shri A C Baria(LM), AB Swich of Zaveripura Tapline of 11 KV Chansad AG was cut by Shri A R Vasava(EA) and Earthing done on incoming side of next AB swich where jumpering work was going on. One of three jumper work has been done. | Awaited | NA | NA | 2 CROSSING ATTEND | NO
9 | COW of Maniya Narsing Waljibhai, MUNIYA FALIYA, Vill-LILVA THAKOR, Tal-Zalod, Dist-Dahod |  |  | 2022-10-08 | FA |  |  | As Per Information Recieved From Sarpanch Shri Gp Lilva Thakor ,The Accident Was Occur Due To Heavy Rain And Wind 11Kv Malvasi Jgy Fdr Conductor Slipped On 11Kv Pin Insulator And Touch On 11 Kv Vcross Arm ,Loose 11Kv Span Due To Sliped Conductor From Pin | AWAITED | NA | NA | Re Stringing And Re Binding Of Conductor As Well As Maintenance Carried Out. | No
10 | RITESHBHAI HASANBHAI RATHWA, Vill-Kosum, Tal-Pavijetpur, Dist-Chhotaudepur |  |  | 2022-10-08 | NFHD |  |  | VICTIM HAS CLIMBED THE LT PSC POLE FOR LT ABC DISMANTLING. ACCIDENTLY A TREE BRANCH FELL ON THE LT LINE & THE LINE SPRUNG AND CAME IN CONTACT WITH THE LIVE HT LINE OF SAJVA AG FEEDER WHICH WAS CROSSING & HENCE GOT ELECTROCUTED. | Awaited | NA | NA | Dismentaling and stringing of LT line work was done on next day, in safety meeting all line staff were instructed to do earthing onboth side and short all 3 conductor | NO
11 | BALVANTBHAI DOLABHAI BHARVAD'S HE BUFFELOW, NR CHAVLA HOTEL, ON CANAL, Vill-Dabhan, Tal-Nadiad, Dist-Kheda |  |  | 2022-10-10 | FA |  |  | DUE TO HEAVY WIND LT LINE CONDUCTOR OF DEGAM AG SNAPPED AND FALL DOWN ON LAND AT THAT TIME HE BUFFELOW OF BALVANTBHAI DOLABHAI BHARVAD PASSING FROM THAT AND HE BUFFELOW COME TO CONTACT WITH CONDUCTOR AND GET ELECTROCUTED AND DIED | AWAITED | NA | NA | Conductor jointed and maintenance carrie out | NO
12 | BUFFALO OF SH BARIYA ABHESINGBHAI JESINGBHAI, JEKOT CHHANGHATI, Tal/Dist-Dahod |  |  | 2022-10-11 | FA |  |  | AS PER INFORMARION RECEIVED IN THE MORNING SH BARIYA ABHESINGBHAI JESINGBHAI WAS TAKING HIS FOUR BUFFALOES TO THE GORGR FOR DRINKING OF WATER.AT THAT TIME ONE BUFFALO WAS ACCIDENTLY TOUCHED THE STAY WIRE AND GOT SHOCK.IT THEN TOUCHED THE BARBED WIRE FENCE | AWAITED | NA | NA | REJUMPERING OF DODP STRUCTURE DONE,PIN INSULATOR WAS INSTALLED | No
13 | jersey cow-Bhikhabhai Ramabhai Rabari, Nr Satyam Apartment, Vill/Tal-Ranoli, Dist-Vadodara |  |  | 2022-10-12 | FA |  |  | Transformer center earth leakage current | Awaited | NA | NA | NEW EARTHING HAS DONE. FENCING HAS BEEN DONE WITH INSULATED WIRE. REPLACEMENT OF ABC CABLE THAT TOUCHES THE RSJ POLE. | NO
14 | Mahesh N Nai, Kalumiya Vad Pase, Vill/Tal-Padra, Dist-Vadodara |  |  | 2022-10-13 | NFHD |  |  | Under the supervision of Shri C S Rathava (LI), Jumper Burnt of Petrol pump Tapline of 11 KV Industrial FDR.So LC Taken of Industrial and Metro feeder by Sh C S Rathava ( LI) and Earthing done on both side of location where jumpering work was going on. | Awaited | NA | NA | Awereness givin to victim during safety meeting | NO
15 | jersey cow-Valabhai Bharwad & Kanubhai Bharwad, Nr Bumleswar Mahadev, Vill-Sankarda, Dist-Vadodara |  |  | 2022-10-13 | FA |  |  | due to fallen of tree Branch LT wire snapped and 2 nos. of cow came to contact with livw wire and electrocuted | Awaited | NA | NA | OPEN CONDUCTOR REPLACED BY ABC . | NO
16 | Balck Buffalow of Lakhabhai Gagubhai Bharvad, At Rasulpura Near bharwad ni jhok, Vill-Changda, Tal-Tarapur, Dist-Anand |  |  | 2022-10-18 | FA |  |  | LT line open conductor is broken and buffallo is electrocuted and died at spot | Regulation 12 & 13 to be observed. | No | No | Rectification done | Yes
17 | BUFFALO OF UDABHAI KABHAIBHAI RATHOD, AT TRAJ VILLAGE NEAR PATEL VADI, Tal-Matar, Dist-Kheda |  |  | 2022-10-24 | FA |  |  | ON DT 24.10.2022 AT APRROX12:15 buffellow (padi)of udabhai kabhaibhai rathod grassing near accident place suddenly came in contact with broken stay wire at dodp which touch DO jumper of 11 KV MANAV JGY fdr and fall down due to electrocuted near dodp and d | AWAITED | NA | NA | Stay wire maintenace carried out and leakage current rectified. | NO
18 | ANIMAL GOAT OF SHREE MUKESHBHAI PARSOTTAMBHAI CHUNARA, NR SMASAN OCHHAN VILAGE MANGROL ROAD, Vill-Ochhan, Tal-Amod, Dist-Bharuch |  |  | 2022-10-27 | FA |  |  | IT SEEMS THERE DOUBLE POLE SWITCH STRUCTURE FOR UNDERGROUND CABLE OF 11 KV MANGROL AG FEEDER VICTIM GOAT WAS GOING TO GRAZING NEAR IT AND CURRENT COMMING IN CONTECT WITH EARTHING GI WIRE WHICH IS CONNECTED TO CABLE EARTH TERMINAL | Awaited | NA | NA | No action required | NO
19 | NARENDRABHAI TRIKAMBHAI DORIYA, B/H HALIPAD , Vill/Tal/Dist-kheda |  |  | 2022-10-17 | FHO |  |  | Victim was working centing work of main gate, which is approx 2.5 ft away from the said line. Accidently came in contact via iron rod with live line. For further tratment, he was shifted to SVP, Ahmedabad. Victim was died on 09.11.2022. | AWAITED | NA | NA | Notice issued to premices owner for Unauthorized work under lline v.l.no Kheda/Tech/8850/29.11.2022 | NO
20 | SANDIP BHATIYA, LEPRECY COMPOUND, Tal/Dist-Vadodara |  |  | 2022-11-02 | NFHD |  |  | Victim was working to removing of 3ph LT temporary connection meter at leprecy ground, ajwa road. Victim was removing service cable connection from meter at that time accidently power supply came in service cable and victim came in contact with live wire and got shocked and burnt his hands. | AWAITED | NA | NA | Awereness givin to victim & co-workers to adopt safe practices during work | NO
21 | BARIA BALVANTBHAI RAMSINGH, FRONT OF NYARA PETROL PUMP NISHAL FALIYA, Vill-Juna Baria, Tal-Devgadhbaria, Dist-Dahod |  |  | 2022-11-25 | NFHO |  |  | As per statement and information received from eye vitness,victim shri Baria Balvantbhai Ramsing was collecting wood at the location and came in contact with the broken conductor and there is a possibility of induction. He was found unconscious at an accident place by our line staff and informed the villagers after that he was transfer to hospital for medical treatment. | AWAITED | NA | NA | AT THAT LOACTION PIN FAULTY WAS FOUND DUE TO WHICH WIRE WAS BROKEN SO PIN WAS REPLACED WITH NEW FIBRE PIN AND 1 SPAN OF NEW WIRE WAS INSTALLED AT THAT LOACTION. | NO
22 | INDRAJIT N RATHOD (EA), KAILASH AUTO GARAGE AB SWITCH,OPP JAGADISH FARASHAN,NEW VIP ROAD, Vadodara |  |  | 2022-12-13 | NFHD |  |  | On dtd : 13.12.2022, 11 KV Aerodrome feeder shutdown is planned for line maintenance activity and LC NO:2039 is taken by LI Shri Bachubhai Ravat at Appx 06:50 AM hrs. Due to underground cable fault by VMSS, power supply of Sai Shrusti tapline of 11 KV Sayaji nagar feeder was transferred on 11KV Aerodrome feeder. Today on dtd :13.12.2022,rectified faulty UG cable of 11 KV Sayaji nagar feeder is rejumpering and during the work of regularizing the power of 11 KV Sayaji nagar feeder on Sai Shrusti t | AWAITED | NA | NA | Awereness givin to victim & co-workers to adopt safe practices during work | NO
23 | Dilipbhai Haribhai Rohit (EA), moraj-chikaliya road, Vill-Moraj, Tal-Tarapur, Dist-Anand |  |  | 2022-12-14 | NFHD |  |  | while attending and completed the jumper work on 11 KV budhej AG Feeder and re shaping of jumper at the same time other feeder 11 KV PR MILL JGY feeder un authorised tree cutting work by unknown person heavy neem branch fallen on 11 KV PR Mill JGY feeder abd pin binding broken and conductor jumped up and came in contact with n11 KV Budhej AG feeder and victim has felt jerk and loosen his physically balance and fallen to grounf form 4th slab of the pole | Awaited | NA | NA | Awereness givin to victim during safety meeting | No
24 | SHRI HARSADBHAI DAHYABHAI, NAHER FALIU, Vill-Kaliyakuva, Tal-Godhra, Dist-Panchmahal |  |  | 2022-12-17 | NFHO |  |  | VICTIM DEMLI CAME FOR DELIVERING BUFFALO AFTER HE PARKED HIS VEHICLE UNDER 11 KV LINE WHERE LINE WAS FILLED UP HE CLIMBED VECHILE CABIN TO UNLOAD LUGGAGE FROM THE CABBIN. HIS HEAD CAME IN CONTACT OF 11 KV LINE AND GOT ELECTROCUTED. WAS ADMITTED IN HOSPITAL | AWAITED | NA | NA | UNDER HT LINE POLE ERECTED TO MAINTAIN GROUND CLEARANCE. | NO
25 | Baria Anilkumar Rameshbhai (VS EA), Tekari faliya, Vill-Abhlod, Tal-Devgadhbaria, Dist-Dahod |  |  | 2022-12-21 | NFHD |  |  | Charging the replace transformer witch was failed earlier and during charging of transformer after cutting of the of the DO of transformer he was joining the LT cable of transformer and also he has seenloose pin of DO on the lower side wich hi was adjusting and thare is possibility accidently came in contact with uper side of DO and gatting electric shock on left hand of the body. | AWAITED | NA | NA | Pin Is Adjusted At The Location Where Accident Takes Place in order to avoid such accidents | NO
26 | Laxmanbhai Bhlabhai Pagi, Vill-Bakor, Tal-Khanpur, Dist-Mahisagar |  |  | 2022-12-22 | FHO |  |  | Victim doing tree cutting on Tree where 11 KV line is passing and during tree cutting got electric shock. | AWAITED | NA | NA | Tree cutting & maintenace work done | NO

## MG SOP3
Name of Distribution Licensee: M G V C L
Quarter : Q-III (Oct-Nov-Dec- 2022)
Year: 2022-23
REGISTER FOR COMPILING THE COMPLAINTS CLASSIFICATIONWISE Q-I 2022-23
Performa SoP 003 B: |  |  |  | APPENDIX-B (already in the SoP regulation)
Classification | Nature of Complaints | Pending complaints of previous qtr. | Complaints received during the qtr. | Total Complaints =2+3 | No. of Complaints redressed during the quarter. |  |  |  |  | Balance Complaints to be redressed. (4) – (9)
[5 empty] | In stipulated time |  | Beyond stipulated time |  | Total (5) to (8)
[5 empty] | Within 50% of stipulated time. | Within stipulated time. | Up to double the stipulated time | More than double the stipulated time
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
A(i) | Loose Connection | 0 | 65722.3465 | 65722.3465 | 32458.2119 | 33264.1346 | 0 | 0 | 65722.3465 | 0
A(ii) | Intruption due to line Break down | 0 | 40138.2843 | 40138.2843 | 18386.7419 | 21751.5424 | 0 | 0 | 40138.2843 | 0
A(iii) | Intruption due to T/C Fail | 0 | 4863.387 | 4863.387 | 2387.5403 | 2475.8468 | 0 | 0 | 4863.387 | 0
B(i) | Quality of power supply,ordinary case which require no Augmentation | 0 | 6650.7896 | 6650.7896 | 4352.6307 | 2298.1589 | 0 | 0 | 6650.7896 | 0
B(ii) | Quality of power supply,ordinary case which require Augmentation | 0 | 4089.2087 | 4089.2087 | 2285.3969 | 1803.8118 | 0 | 0 | 4089.2087 | 0
C(i) | Meters- Stoped/Defective meter | 0 | 14726.9728 | 14726.9728 | 8639.9315 | 6087.0413 | 0 | 0 | 14726.9728 | 0
C(ii) | Meters- Billing on average basis for > two bills | 0 | 5470.399 | 5470.399 | 3335.2415 | 2135.1575 | 0 | 0 | 5470.399 | 0
D(i) | Over head lines - loose wires | 0 | 5111.9407 | 5111.9407 | 2666.667 | 2445.2737 | 0 | 0 | 5111.9407 | 0
D(ii) | Over head lines - in adiquate ground clearance | 0 | 1518.1995 | 1518.1995 | 1041.5823 | 476.6172 | 0 | 0 | 1518.1995 | 0
E(i) | Bills- for current bills where no addl information required | 0 | 3967.0519 | 3967.0519 | 3024.3254 | 942.7266 | 0 | 0 | 3967.0519 | 0
E(ii) | Bills- for current bills where addl information required | 0 | 2903.6215 | 2903.6215 | 1640.4276 | 1263.1939 | 0 | 0 | 2903.6215 | 0
F(i) | Service connections- where extention of mains is not required | 0 | 8480.7532 | 8480.7532 | 6018.7476 | 2462.0057 | 0 | 0 | 8480.7532 | 0
F(ii) | Service connections- where extention of mains is required | 0 | 4515.0904 | 4515.0904 | 2205.6408 | 2309.4496 | 0 | 0 | 4515.0904 | 0
F(iii) | Service connections- Modification in connected load | 0 | 2925.8902 | 2925.8902 | 1175.0963 | 1750.7939 | 0 | 0 | 2925.8902 | 0
F(iv) | Service connections- Name change/reconnection | 0 | 3160.124 | 3160.124 | 1547.1218 | 1613.0021 | 0 | 0 | 3160.124 | 0
G | Refund of amount due inregard to temp conn | 0 | 487.9244 | 487.9244 | 242.5471 | 245.3773 | 0 | 0 | 487.9244 | 0
H | Others | 0 | 20590.0163 | 20590.0163 | 10555.5509 | 10034.4654 | 0 | 0 | 20590.0163 | 0
| TOTAL | 0 | 195322 | 195322 | 101963.4015 | 93358.5985 | 0 | 0 | 195322 | 0
The format is to be sent quarterly
The quarterly reporting of the year means reporting for the period 1st Quarter as Jan – Mar, 2nd Quarter as Apr – Jun, 3rd Quarter as Jul – Sep and 4th Quarter as Oct – Dec of the year.
For any other complaints not mentioned in the classification, the sequence for (H) can be used.

## MG SoP 04
Name of Distribution Licensee: M G V C L
Quarter : Q-IV (Oct-Nov-Dec- 2022)
Year: 2022-23
Performa SoP 004 : Publicity carried out while displaying the contact details of consumer complaints centers
Particulars should also cover the details of consumer awareness program conducted, advertisement done through various media like TV, newspaper, radio, pamphlets & booklet distributions, Displays etc. The development of website and any medium through which public education is carried out can be included.
Sr. No | Actions or steps carried out by distribution licensee towards public awareness in the quarter | Likely number of consumers influenced
1 | RTI Officers Name is displayed at customer care centre on each office | 3462678
2 | Necessary information regarding time schedule for new connection and solving complaints is display on the board. | 3462678
3 | Contact nos. of various officers of the company for emergency contact is also displayed at customer care centre. | 3462678
4 | Displayed safety posters at various S/dn,Divisions | 5000
5 | Safety Meeting with Line Staff at various S/dn,Divisions on Every Monday (Line staff influenced) | 13800

## SOP-05
Name of Distribution Licensee: M G V C L
SOP Q-III (oct-Nov-Dec-22)
Year :2022-23
Performa – SoP 005 B: Action taken report by the Redressal Committee
Sr. No | Month | Date and Time Meeting conducted | No of complaints registered at the meeting | No. of complaints pending at the end of the meeting
1 | 1st Month of the quarter (Oct'22) | 28.10.22,11.30 am at Corporate Office | 4 | 0
2 | 2nd Month of the quarter (Nov'22) | 24.11.22,11.30 am at Godhra Office | 2 | 0
3 | 3rd Month of the quarter (Dec'22) | 17.12.22,11.30 am at Corporate Office | 4 | 0

## MG SoP - 06
Name of Distribution Licensee: M G V C L
Financial Year: 2022-23
Quarter : Q-III (Oct-Nov-Dec-2022 )
Performa SoP 006: Failure of Distribution Transformer
Sr. No. | Name of Circle | Nos. of existing Distribution Transformers at the start of the quarter | Nos. of Distribution Transformers added during the quarter | Total number of Distribution Transformers on end of quarter | Total number of Distribution transformer failed during quarter-III | % failure rate of Distribution transformer
|  | A | B | C=A+B | D | H = (D)*100/C
1 | Baroda O&M | 53182 | 800 | 53982 | 1086 | 2.0118
2 | Baroda City | 9191 | 177 | 9368 | 17 | 0.18147
3 | Anand | 24454 | 418 | 24872 | 155 | 0.62319
4 | Nadiad | 31174 | 696 | 31870 | 307 | 0.96329
5 | Godhra | 59587 | 1294 | 60881 | 1205 | 1.9793
| MGVCL | 177588 | 3385 | 180973 | 2770 | 1.5306

## SoP008
Name of Distribution Licensee: M G V C L
SOP:Qtr.III(OCT-NOV-DEC-22)
YEAR:2022-2023
Performa SoP 008: Sample Test result for Neutral Voltage
Compliance Sample Test Report for Neutral Voltage
-1 | -2 | -3 | -4 | -5 | -6
Sr. No | Category of consumers | Sample Size | Standard specified in regulation | Deviation of results from the sample test (Numbers) | % age compliance
|  | (Numbers) |  |  | (6) = (5)*100/(3)
| LT consumers | 1368 | 2% | 0 | 0
1 | Domestic | 975 | 2% | 0 | 0
2 | Commercial | 190 | 2% | 0 | 0
3 | Industrial | 12 | 2% | 0 | 0
4 | Agricultural | 97 | 2% | 0 | 0
5 | Public water works | 6 | 2% | 0 | 0
| HT consumers |  | 2%
6 | HT industrial | 6 | 2% | 0 | 0

## SoP009
Name of Distribution Licensee: M G V C L
SOP:Qtr.III(OCT-NOV-DEC-22)
YEAR:2022-2023
Performa SoP 009: Sample Test result for Voltage variations
Compliance Sample Test Report for voltage variations
-1 | -2 | -3 | -4 | -5
Voltage Level | Sample Size (numbers) | Limit or prescribed standard | Deviation of results from the sample test (Numbers) | % age compliance
(5) = (4)*100/(2)
Low Voltage | 5 | +6% to -6% | 0 | 0
High Voltage | 2 | +6% to -9% | 0 | 0
Extra High Voltage | 1 | +10% to -12.50% | 0 | 0

## SoP010
Name of Distribution Licensee: M G V C L
SOP:Qtr.III(OCT-NOV-DEC-22)
YEAR:2022-2023
Performa SoP 010: Sample Test result for Harmonics
Compliance Sample Test Report for Harmonics
-1 | -2 | -3 | -4 | -5 | -6
Sr. No | Category of consumers | Sample size (Numbers) | Limit or standard prescribed | Deviation of results from the sample test (Numbers) | %age compliance
(6) = (5)*100/(3)
1 | LT consumers | 16 | 3.5% | 0 | 0
2 | HT consumers | 2 | 3% | 0 | 0
3 | EHT consumers | 1 | 3% | 0 | 0
Note: The licensee shall also submit along with the above harmonic data, the records of customer wise drawls of harmonic currents measured at various strategic points.
The formats SoP 008, SoP 009 and SoP 010 have to be sent annually.
For the purpose of annual submissions, the year end has to be considered as the end of December month of a particular year.

## 11A
Q-3(Oct-Dec-22)
Year: 2022-23
SoP 011 –A: System Average Interruption Frequency Index (SAIFI)
Sr. No | Month | Ni - Total no of customers for each momentary interruptions | NT - Total no of customers served |  |  | Past year corrosponding Month
1 | 2 | 3 | 4 | 5 | 6=5/4
1 | Oct' 22 | 3172447 | 3445410 | 11285658 | 3.2756 | 3.7029
2 | Nov' 22 | 3161852 | 3458582 | 8375291 | 2.4216 | 2.6592
3 | Dec' 22 | 3182318 | 3462678 | 7842856 | 2.265 | 3.3132
|  |  | 10366670 | 27503805 | 2.6531 | 3.2243

## 11B
Q-3(Oct-Dec-22)
Year: 2022-23
SoP 011 – B System Average Interruption Duration Index (SAIDI)
Sr. No | Month | ri = Restoration Time for each interruption event | Ni - no of interrupted customers for each sustained interruption event | ri * Ni – Total customer interruption Duration | ri=Restoration Time for each interruption event | Ni= No of Interrupted customers for each sustained Interruption | NT - Total no of customers served | Customer Interruption Duration |  |  | Past year corrosponding Months
[9 empty] | MINS. | HRS.
1 | 2 | 3 | 4 | 5= 3 X 4 | 3 | 4 | 5 | 6 | 7=4/3 | 7A | MINS. | HRS.
1 | Oct' 22 | July |  |  | 674254 | 3172447 | 3445410 | 804235072 | 233.4222 | 0.16181 | 297.2582 | 0.20625
2 | Nov' 22 | August |  |  | 614612 | 3161852 | 3458582 | 785896490 | 227.2308 | 0.15764 | 227.7268 | 0.15833
3 | Dec' 22 |  |  |  | 551485 | 3182318 | 3462678 | 680027792 | 196.3878 | 0.13611 | 236.2634 | 0.16389
[6 empty] | 9516617 | 10366670 | 2270159354 | 218.9864 | 3.64 | 253.699 | 0.17639

## 11C
Q-3(Oct-Dec-22)
Year: 2022-23
SoP 011 – C: Momentary Average Interruption Frequency Index (MAIFI)
Sr. No | Month | Number of Momentary interruptions Imi | Nmi - Total no of customers for each momentary interruptions | NT - Total no of customers served |  |  | Past year corrosponding Month
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | Oct' 22 | 22671 | 2982664 | 3445410 | 35437406 | 10.2854 | 9.7871
2 | Nov' 22 | 19245 | 2935378 | 3458582 | 29507855 | 8.5318 | 8.8207
3 | Dec' 22 | 17625 | 2957731 | 3462678 | 27955571 | 8.0734 | 8.5418
|  |  |  | 10366670 | 92900832 | 8.9615 | 9.0492

## MG SoP - 13
Name of Distribution Licensee: M G V C L
Financial Year: 2022-23
Quarter : Q-III (Oct-Nov-Dec-2022 )
Performa SoP 013: Faulty Meters Replacement
Consumer Category | No. of faulty meters at the start of the quarter | No. of faulty meters added during the quarter | Total no. of defective / faulty Meter | No. of faulty Meters repaired and replaced | No of faulty meters pending at the end of the quarter | Remark
| 1 | 2 | (3)=(2)+(1) | 4 | (5)=(3)-(4)
1 PHASE
MGVCL | 6469 | 26933 | 33402 | 26150 | 7252
3 PHASE
MGVCL | 1620 | 3411 | 5031 | 4421 | 610

## MG SoP 16
Name of Distribution Licensee: M G V C L
Quarter : Q-3 (Oct-Nov-Dec- 2022)
Year: 2022-23
Performa SoP 016: Compensation details
COMPENSATION DETAILS
Sr.No. | Event | Compensation | No of cases where compensation was given (in numbers) | Amt of compensation paid (in Rs.)
1 | Duty to provide supply | Rs. 50 per day of delay from the limit specified in the performance regulations | 0 | 0
| a) New Connection |  | 0 | 0
| b) Additional Load |  | 0 | 0
| c) Temporary supply |  | 0 | 0
| d) Shifting service connection |  | 0 | 0
| e)Transfer of service connection |  | 0 | 0
| f) Change in tariff category of consumer |  | 0 | 0
2 | Complaints in billing | Rs. 50 for non reply within the period prescribed in Regulations | 0 | 0
3 | Replacement of meters | LT- Rs. 25 per day of delay - maximum Rs.2,500 and HT - Rs. 250 per day of delay - maximum of Rs.5,000 | 0 | 0
4 | Interruption of supply | LT- Rs. 25 for every 6 hrs of delay- maximum of Rs. 500 and HT- Rs. 50 for every 6 hrs delay- maximum Rs. 1000/- | 0 | 0
5 | Voltage fluctuations and complaints | Rs. 50 for failure to visit or convey findings within the stipulated period | 0 | 0
6 | Responding to consumer's complaints | Rs. 25 for each day of delay- maximum Rs. 500 | 0 | 0
7 | Grievance Handling | Rs.25 for failure in handling grievance | 0 | 0
TOTAL |  |  | 0 | 0