## MG COVER PAGE
Name of Distribution Licensee: M.G.V.C.L.
Quarter of the year : Q-III (Oct-Nov-Dec-2025)
Year: 2025-26

## MG SoP 01
Name of Distribution Licensee: M G V C L
Quarter III (Oct-25 to Dec-25)
Year:2025-26
Performa - SoP 001: Fatal and Non-fatal accident report
NUMBER OF ACCIDENTS FOR THE 3rd QUARTER 2025-26
Sr. No | Name of Area/Circle | No of accidents in the quarter |  |  |  |  | Cumulative since the first quarter of the current FY year
|  | Departmental |  | Outsider |  |  | Departmental |  | Outsider
|  | FH | NFH | FH | FA | NFH | FH | NFH | FH | FA | NFH
1 | Baroda City | 0 | 0 | 1 | 0 | 0 |  | 1 | 6 | 1
2 | Baroda (O&M) | 1 | 1 | 1 | 7 | 1 | 1 | 2 | 11 | 27 | 1
3 | Anand | 0 | 0 | 3 | 0 | 1 | 2 | 1 | 11 | 12 | 3
4 | Godhra | 0 | 1 | 4(1-Pvt) | 1 | 1 | 1 | 1 | 17(4-Pvt) | 31 | 6
5 | Nadiad | 0 | 0 | 0 | 3 | 2 |  | 2 | 7 | 23 | 8
| TOTAL | 1 | 2 | 9 (1-Pvt) | 11 | 5 | 4 | 7 | 52 (4-Pvt) | 94 | 18
[6 empty] | 28 |  |  |  |  | 175
FH – Fatal Human, FA – Fatal Animal, NFH – Non-fatal Human
The format is to be sent quarterly

## MG SoP 01 (GERC) (hidden)
Name of Distribution Licensee: M G V C L
Quarter I (Apr-25 to Jun-25)
Year:2025-26
Performa - SoP 001: Fatal and Non-Fatal electrical accident report
NUMBER OF ACCIDENTS FOR THE 1st QUARTER OF 2025-26
Sr. No | Name of Area/Circle | No of accidents in the quarter |  |  |  |  | Cumulative since the first quarter of the current FY 2024-25
|  | Departmental |  | Outside |  |  | TOTAL
|  | FH | NFH | FH | FA | NFH | FH | FA | NFH
1 | Baroda (City) |  |  | 2 | 1 |  | 2 | 1
2 | Baroda (O&M) |  | 1 | 8 | 12 |  | 8 | 12
3 | Anand |  | 1 | 4 | 8 | 2 | 4 | 8 | 2
4 | Godhra |  |  | 6(1-Pvt) | 15 | 3 | 6(1-Pvt) | 15 | 3
5 | Nadiad |  | 2 | 6 | 7 | 1 | 6 | 7 | 1
| TOTAL | 0 | 4 | 26 (1-Pvt) | 43 | 6 | 26 (1-Pvt) | 43 | 6
FH – Fatal Human, FA – Fatal Animal, NFH – Non-fatal Human | [5 empty] | 79 |  |  | 75
PVT - Private Premises Accident.

## SoP 002
Performa – SoP 002: Action taken report for safety measures complied for the accidents occurred
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
Sr. No | Location of Accident and details of the victim | Date of occurrence | Type of Accident | Installation |  | Accident Type |  |  | Cause of Accident | Findings of CEI / EI / AEI | Remedies suggested by CEI /EI / AEI in various cases | Whether the remedy suggested is complied | Action taken to avoid recurrence of such Accident | CEI REPORT received YES/NO | If No then , mention letter no. and date written to CEI/EI/AEI office. | Findings of CEI / EI / AEI | Remedies suggested by CEI /EI / AEI in various cases | Whether the remedy suggested is complied | Action taken to avoid recurrence of such Accident | Amount of compensation and date of compensation paid | Circle office | Division | Sub-division | Reason
1 | Sujaben Ramjibhai Gohel,Near JIO Tower,Vill-Fatepura,Tal-Tarapur,Dist-Anand | 2025-10-08 | NFHO | [5 empty] | As per the statement of pancho’s and eye witness victim as per above (8a1) farming grass to cow there nearby 11 kv kasbara ag dom feeder is passing. The distance from ground of 11 kv line wire is around 3 feet height due to psc pole broken , nearby victim framing grass to cow directly came in touch with 11 kv line and got electrocuted. After it the victim is transferred to khambhat , cardiya care hospital for further treatment in private vehical, at present asking to victim relative she is und | [6 empty] | CEI Report Pending |  |  | લાઇન ખેચી પોલ સીધા કરી અને ક્લીયરન્સ કરી લાઇન ચાલુ કરેલ છે | Pending due to medical Report not submitted | Anand | Petlad | Tarapur
2 | Parbatbhai Shivabhai Parmar,Boria Vistar,Vill-Kothipura,Tal-Mahemdabad,Dist-Kheda | 2025-10-11 | FA | [5 empty] | As per buffaloes owner's statment buffaloes were passing from in the farm of sh kantibhai dahyabhai parmar farm and while passing near the duble pole do structure center buffalo had starded scrathing with do structure guy wire during this scraqthing guy wire broken from bottom side and touch with b phase do buffalo came in contact with guy wire and due to leakage current in the guy wire thr buffalo got electrocuted | [6 empty] | Awaited |  |  | IMMEDIATELY AFTER GATTING INFO STAFF RUSHED TO THE SITE AND THEY HAVE DISCONNECT GUY WIRE FROM DOUBLE POLE DO STRUCTURE | 15000/28.11.2025 | Nadiad | Mehmdabad | Haldarwas
3 | Bhabhor Rinkeshbhai Lalsingbhai,Vill-Bhamela,Tal-Sanjeli,Dist-Dahod | 2025-10-19 | FHO | [5 empty] | To maintain uninterrupted power supply, the work of replacing the failed transformer is given to the agency of m r patel contractor, in which they have to strict instruction were also given to work using safety equipment and inform the staff of the office in each village and replace the transformer in their presence, but on 19/10/2025, they went to replace the transformer without informing the staff on 19/10/2025, 12:45 the contractor telephoned the office here and informed us that a laborer go | [6 empty] | AWAITED | NA | NA | All staff have been informed to take L.C. before starting work on the line and to earth all phases of the line. They have also been instructed to use safety tools during work. Weekly meetings are being arranged with staff, during which all personnel are instructed to work strictly as per safety norms and to ensure proper use of safety tools | Contractor person | Godhra | Dahod | Zalod
4 | Arshdipsinh Jagroop sinh,Near canal,Vill-Deva Talpad,Ta-Sojitra,Dist: Kheda | 2025-10-20 | NFHO | [5 empty] | As per the statement of pancho and farm owner during crop cutting (dangar) through harvester machine victim cheking crop removal behind harvester machine and touched back side of machine and suddenly got electric shocked and fell down to earth. Immediately called 108 by owner of farm. Victim has minor skin burnt in left hand and right leg.victim health is stable. | [9 empty] | The tilted pole was strightened& line was restringing to maintain the heighgt from the ground as per specification |  | Nadiad | Nadiad City | Vaso
5 | Tarabada Girishbhai Dalsukhbhai.Vill-Karakhadi,Ta-Padra,Dist: Vadodara | 2025-10-24 | NFHO | [5 empty] | On 24-10-2025, at around 11:30 am, shri girishbhai dalsukhbhai talpada was climbing on the shed above the lilagari mata temple in karkhadi village and was cutting the branches of a nearby tree with a sickle. While cutting the branches, he stepped back and touched the 11 kv dudhwada ag feeder line passing above the shed and he was electrocuted in the back of his body. After that he was admitted in the crossroad hospital for medical treatment. | [6 empty] | Awaited | NA | NA | notice issued for illegal construction vide letter no. Mobha/tech/415 Date:13.03.2025 | NA | Baroda (O & M) | Jambuva | Mobha
6 | Buffalo of Baria Babubhai Chhotubhai,Vill-Bhadrali,Tal-Bodeli,Dist-Chhotaudepur | 2025-10-24 | FA | [5 empty] | Shri bria babubhai chhotubhai with his cows and buffaloes were returning home home after grazing. A pregnant buffalo got contact with stay wire suddenly leakage current pass though stay wire and a buffaloes died due to electrocution | [6 empty] | Awaited | NA | NA | New Stay provided | 15000 under Process | Baroda (O & M) | Bodeli | Bodeli
7 | Calf of Bharwad Sevabhai Revabhai,Maninagar socity gate,Vill-Ali Kherva,Tal-Bodeli,Dist-Chhotaudepur | 2025-10-26 | FA | [5 empty] | Shri bharvad sevabhai revabhai was grasing hs chalf cows and buffaloes the calf came into contact with the earthing wire of the transformer near the water works of alikherva panchayat .due to rutrn power from the wate works connection the calf got electrocution. | [6 empty] | Awaited | NA | NA | Earthing Reactivated, PVC Pipe Provided | 8000 under Process | Baroda (O & M) | Bodeli | Bodeli
8 | Buffalo of Boliya Sajan Revabhai,Near Pathik Park,Vill-Karjan,Tal-Karjan,Dist-Vadodara | 2025-10-27 | FA | [5 empty] | On dtd. 27.10.25 time approx 11:00am buffalo passing from prathik park party plot and lt abc line suddenly breckdown and buffalo got touch in live conductor. | [6 empty] | Yes | As per CEI Report conductor snapped due to heacy rain and Cyclone | Rejoined | Rejoined LT Line | NA | Baroda (O & M) | Jambuva | Karjan-II
9 | Dineshbhai Govindbhai Solanki,Vill-Dharmaj,Tal-Petlad,Dist-Anand | 2025-10-26 | FHO | [5 empty] | 40 yrs old mr dineshbhai govindbhai solanki residing of vill-saijpur ta.borsad who met an electrical fatal accident on 11 kv ras ag dom feeder emanating from 66 kv virsad s/s on 26.10.2025, mr dineshbhai climbed on pole and get connected to live wire and accident occured | [6 empty] | CEI Report Pending |  |  | NA | Legal Heir not found | Anand | Petlad | Petlad R
10 | Unknown COW,Near green park soc,Vil-Dabhan,Ta-Nadiad,Dist-Kheda | 2025-10-27 | FA | [5 empty] | As per the statement of pancho’s lt ab 2 wire was tied to near by telephone steel tower almost 3 meter away from main lt pole , wire binding lt to steel pole as long span across street , while cow passing near pole at touched to steel pole where leaked current | [9 empty] | ABC 2 wire were detachched from telephone pole & restringing properly to prevent accident |  | Nadiad | Nadiad | Nadiad R
11 | Mulani Sukhdevbhai HarjivanbhaiNear,Siddhi GIDC Gate,Vill-Waghodia,Tal-Waghodia,Dist-Vadodara | 2025-10-28 | FHO | [5 empty] | Victim was working for streetlight maitenance work under siddhi gidc privetely. While shifting of metal ladder having hieght of approximately 23 to 24 feet under by 11 kv pipariya ag feeder victim came in contact with live 11 kv conductor. The ownership of the said feeder is of khatamba sdn and also portion where the accident occured is also maintain by them but the area falla under waghodia sdn juridiction. Hence waghodia sdn has processed for the accident. | [6 empty] | Awaited | N.A. | N.A. | As per site sketch and DE Waghodia investigation report, ground clearance of HT line is 23 to 24 ft. which is within permissible limit as per CEA regulation Cl No. 60 Schedule VIII A. | Office Note issued for payment to Exp. Section dated: 16.01.26 (Under process) | Baroda (O & M) | Baroda O & M | Khatamba
12 | Buffalo,Vill-Bhadrali,Tal-Bodeli,Dist-Chhotaudepur | 2025-10-30 | FA | [5 empty] | During the site visit, it was found that on 30.10.2025 at about 01:00 hrs, under the 11 kv jojva ag feeder emanating from 66 kv surya substation, near laxmanbhai farm, bhadrali, a fatal animal accident had occurred. Shri bariya laxmanbhai’s wife smt. Kailashben was grazing cows and buffaloes, when one female buffalo (approx. 8 years old) forcefully shook the do stay wire. At the time of contact, the stay wire had come into touch with the jumper, resulting in electrical potential on the stay wire | [6 empty] | Awaited | NA | NA | New Stay provided | 15000 under Process | Baroda (O & M) | Bodeli | Bodeli
13 | Kalubhai Jogabhai Pandor,Navi Vasahat,Vill-Khanta,Tal-Virpur,Dist-Mahisagar | 2025-08-21 | FHO | [5 empty] | On 21.08.2025, at approximately 17.00 Hrs. The victim, a hired laborer, was assigned the task of cutting a Limda tree at Village Khata-2 (Navi Vasahat), on the farm of Shri Shanabhai Kalubhai Pagi. The tree was located beneath the 11KV Koydam AG feeder. While cutting the tree branches, one branch fell onto the 11KV line. The victim attempted to remove the fallen branch using a cutter machine, during which he came in contact with the live line and was electrocuted. | [6 empty] | AWAITED | NA | NA | Village-level safety awareness programs were conducted at the Gram Panchayat Offices of Nasroli and Kheroli. Safety pamphlets were distributed, and discussions were held on maintaining proper line clearance | Initial Rs.1.00 Lakh paid on dtd 09.12.2025 | Godhra | Lunawada | Virpur
14 | Bullock,Vill-Raneda,Ta-Naswadi.Dist-Chotaudepur | 2025-11-02 | FA | [5 empty] | As Per Site Visit And Statement Of Eye Witness and the Owner of the bullock, in the morning , Shri Devenrabhai Narayanbhai Rathwa (the Owner of the bullock) went to his farm along with his bullock for grassing and going to his farm along with the bullock. An 11 KV Kandha AG feeder line crosses the route leading to his farm. While passing through the location at around 09:32 hours approximately, a fault occured due to pin punctured, resulting in the conductor breaking and falling to the ground, T | [6 empty] | Awaited | NA | NA | Pin insulator replaced and conductor re joined | 15000 under Process | Baroda (O & M) | Bodeli | Naswadi
15 | Ashishkumar Satishbhai Patel,Patel Faliyu,Vill-Chenpur,Ta-Devgadhbaria.Dist-Dahod | 2025-11-04 | FHO | [5 empty] | Human fatal accident at,patel faliya,Chenpur Ashishbhai satishbhai patel was playing near his home while the said neutral conductor snapped accidentally and the child was contact with neutral conductor directly to his back part and suddenly he was electrocuted and declared dead by doctor later on. | [6 empty] | AWAITED | NA | NA | Maintenance work has been carried out, and the open LT line has been replaced with LT-LT ABC, along with restringing of the LT line | CONSENT PENDING INFORMED WIDE L.NO.11394/31.12.2025 | Godhra | Dahod | Devgadh Baria
16 | Bharatkumar Manilal Makwana,Vill-Ukardi,Ta-Lunawada.Dist-Mahisagar | 2025-11-06 | NFHD | [5 empty] | On Dtd 06 Nov 2025 Sh. B M Makwana (EA) And Sh. N P Patel (EA) Were At Night Duty. During Their Duty At About 22:37 Hrs In Night There Was A Complain Received Of Broken Pole By Dumper At Ukardi Village At Complain Center. To Attend This Complain Sh. B M Makwana Sh. N P Patel And 2 FRT Staff Were Reached To Ukardi Village With FRT Vehicle. After Reached To Ukardi Village Sh. N P Patel Was Taking Photographs Of Dumper And Broken LT Poles. Meanwhile Sh. B M Makwana Was Going For Dismantelling Of LT Cable From LT Bushing Of TC. By Making Power Off Of 11 KV Nani Denavad AG Instead Of 11 KV Chavadiya AG From Where The Said TC Is Getting Power. While B M Makwana Was Climbing On TC To Dismantle LT Line From LT Bushing Without Removing DO Fuses On TC Structure He Aacidentally Came In Contact With HT Jumper On TC And Got Electrocuted. | [6 empty] | AWAITED | NA | NA | New pole numbering has been carried out. Transformer DO fuse and distribution box have been replaced. The damaged LT pole has been dismantled and a new pole has been erected in its place | Departmental | Godhra | Lunawada | Lunawada -I
17 | Ratansing Natwarsing Barot,Sudama Nagar,Vill-Gotri,Tal-Vadodara,Dist-Vadodara | 2025-11-07 | FHO | [5 empty] | As Per Site Visit And The Statement Of The Victims Sonsthe Victim Was Suffering From Mental Illness And Breathinhg Issue And The Victim Had Intentionally Climbed On The Tc Structure And May Have Come Into Contact With The Live Part Of The Transformer And Got Elecrocuted | [6 empty] | CEI report not received | NA | NA | The fencing is provided around TC DP. | As Police Panchnama is not received till date and letter written to police station vide lette no: GSD/T/HR/17, DT:05.01.2026. So compansatison is pending. | Baroda City | Vishwamitri W | Gotri
18 | 1 Buffalo She 1 Cow She,Vill-Sathod,Tal-Dabhoi,Dist-Vadodara | 2025-11-08 | FA | [5 empty] | A buffalo and cow were grazing in the field near nada ni vadi sathod near canal then suddenly they may get touch 11 kv tharvasa ag HT LINE which had already fell down due to heavy rain and cyclone.The section of where accident occured was alredy cut off.Unknown person may be charged this section.The investigation is ongoing about this matter.The dio section were alredy cut off due to water loging. They died on the site may be due to electrocution. The real cause of death of the 2 animal will | [6 empty] | Awaited /L.NO DBH/T/L/C/11364 & DT:10-11-2025 | NA | NA | 2 Nos New Pole in Long Span Ht line & 3 Span HT restrinigng done | (1) 15000-/ & CV NO:89 BY NEFT/ 12-12-2025 & (2) CV NO:-88/ DT:-12-12-2025 & CEI REPORT PEDNING | Baroda (O & M) | Dabhoi | Dabhoi
19 | Nayankumar Chunilal Dabhi,Vill-Samsabad,Tal-Vadodara,Dist-Vadodara | Accident Date:- 11-11-2025 Became FHD Date:-03-12-25 | FHD | [5 empty] | The Jumper On The RSJ Shackle Pole Was Indeed Broken. Creepers Were Found Entangled On The Top Portion Of The Pole. The Concerned Consumers Were Actually Receiving Supply From The 11 Kv Dangkikuva AGDOM Feeder, Not The Feeder For Which Line Clear Permit Was Taken. Verification At 66 Kv Karvan Substation Confirmed A Transient Tripping At 14:05 On The Y And B Phases Of The 11 Kv Dangkikuva AGDOM Feeder | [6 empty] | Awaited | NA | NA | Accident occurred due to wrong line clear permit taken by victim oniy. No other action required at site. | NA | Baroda (O & M) | Jambuva | Jambuva
20 | Owner-Rohit Jashwantbhai Devjibhai,Vill-Devki Ansol,Tal-Mehmdabad,Dist-Kheda | 2025-11-23 | FA | [5 empty] | When She Buffalo was passing from Morarbhai Mithabhai Parmar’s farm, and while passing near the iron wire fencing, Buffalo’s horn stucked in fencing got electric shock and died on spot. Further it was found that about 50 meters away earthing wire of LT psc pole fell on iron fencing and leakage current passed through it caused death of buffalo. Furthermore leakage current in earth wire found due to bird shorted on C clamp of LT line. | [6 empty] | Awaited |  |  | New Earthing Of LT Pole And Pure Cause (Shorted Bird Between Wire And C Clamp) Removed. | 15000/Underpayment | Nadiad | Mehmdabad | Mehmdabad
21 | 1) Gamit Vilsanbhai Vaneshbhai,2)Vasava Sunilbhai Utariyabhai,3) Vasava Nileshkumar Rajeshbhai, 4) Vasava Veneshbhai Pratapbhai,Near Ambika Hotel,Vill-Fagvel,Tal-Kathlal,Dist-Kheda | 2025-12-04 | NFHO | [5 empty] | On 4 DEC 2025, It Was Goda Poonam In Fagvel Village. Like Every Year, All The Vehicles With Djs From Outside Come To Fagvel To Have Darshan Of Bhathiji. On That Day, On 4 DEC 2025, At Around 6 Pm, A DJ Equipped Vehicle Came From Outside To The Open Plot Next To Ambika Hotel And About Seven To Eight People Were Sitting On That DJ Equipped Vehicle. While Taking That DJ Equipped Vehicle To The Open Plot, The Man Sitting On The DJ Equipped Vehicle Got Electrocuted By The Live Line Of The Electron 11 KV Kailasnath JGY Passing Through That Open Plot. After That, The Four Boys Who Were The Victims At That Time Were Immediately Called 108 Ambulance And Taken To The Nearest Hospital For Treatment. The Four Men Were Taken To The Carewell Hospital At Kathlal By 108 Ambulance. Further, On 6 DEC 2025 At 11:15 Am, Nareshbhai Bharatbhai Rathod Informed The MGVCL Officer That The Above Incident Had Taken Place On 4 DEC 2025 In The Evening. Therefore, While Inspecting The Spot, Looking Around, The Open Space In Which The DJ Vehicle Was Parked, About Two Meters Of Soil Has Been Filled In That Open Plot, So That The Distance Between The Lines As Per The Company's Rules Should Not Be There, Due To Which This Accident Has Occurred. The Truck Number Is GJ 23 X 9967 And The Height Of The DJ Vehicle Is About 12 To 13 Feet. | [6 empty] | Awaited |  |  | 2 NOS Of RSJ Poles With Extension Have Been Erected For even Higher Ground Clearance | PENDING | Nadiad | Nadiad O & M | Balasinor 2
22 | Jayveersinh Dilipsinh Raj,Nava Ghara Vistar,Vill-Bhanpura,Tal-Anklav,Dist-Anand | 2025-12-13 | FHO | [5 empty] | On dated 14.12.2025 site visited for electrical Accident occurred on 13.12.2025 at Bhanpura village has been done. During site visit An Information received from Victim's Father that victim flying kite on ground near house and kite stuck in 11 kv of bhanpura ag feeder open conductor line under which construction work has been done by victim's family. So Clarence between line and terrace is very low. Victim goes to terrace to take kite from 11 kv conductor and may came in contact with 11 kv condu | [6 empty] | CEI Report Pending |  |  | NA | Legal Heir not found | Anand | Borsad | Asodar
23 | Damor Raysingbhai Valabhai,Damor Faliyu,Vill-Ladan na muvada,Tal-Khanpur,Dist-Mahisagar | 2025-12-14 | FHO (Pvt) | [5 empty] | Roj kam done. Actual reason of accident unknown | [6 empty] | AWAITED | NA | NA | N.A | private premises | Godhra | Lunawada | Bakor
24 | Ravindrakumr Ranaram Sing,Vill-Rohini,Tal-Khambhat,Dist-Anand | 2025-12-15 | FHO | [5 empty] | Accidentally contact with conductor of 11 kv feeder while cleaning the cutter machine which was parked below 11 kv ht line | [6 empty] | CEI PENDING | - | - | LINE SHIFTING DONE | NO COMPENSATION DONE , IN PM REPORT ELECTROCUTION IS SHOWN AS PROBABLE CAUSE OF & FINAL CAUSE OF DEATH WILL BE GIVEN AFTER FSL REPORT | Anand | Petlad | Cambay R
25 | Bullock of Shri Baria Vitthalbhai Ramsinh,Nava Faliya,Vill-Vav,Tal-Ghoghamba,Dist-Panchmahal | 2025-12-15 | FA | [5 empty] | ON DTD. 15.12.2025 AT Vav(Nava Faliya) Village A bullock of Shri Vitthalbhai Ramsinh Baria was tied with rope in front of his house.Moreover 11 KV Vakod Agdom Feeder line is Passing through in front of Shri Vitthalbhai Ramsinh Baria's House.Around 11:00 Hrs Due to pin puncture in that particular Tapline of 11 KV Vakod AGDom feeder was accidentally Snapped and fell on the Bullock and due to that Bullock was electrocuted and fell down on land and died on spot.Cause of death and detail investigatio | [6 empty] | AWAITED | NA | NA | The pin has been replaced, the wire joint has been properly carried out, and the power supply has been restored | Letter written for insufficient 156/19.01.2026 | Godhra | Halol | Ghoghamba
26 | Rajendra Shivabhai Parmar,Ghansar Vav,Vill-Vav,Tal-Halol,Dist-Panchmahal | 2025-12-23 | NFHO | [5 empty] | On 23.12.25, during the afternoon hours, the victim was engaged in routine agricultural water-related activities in his farm. An LT line originating from a 63 kVA distribution transformer, supplying power to four agricultural connections, passes through the said agricultural field. - As per the statements of eyewitnesses, several doves were sitting on the LT line near the second span from the transformer. After some time, the birds flew away together, which caused disturbance and overlapping of | [6 empty] | AWAITED | NA | NA | The existing bare conductor has been replaced with AB cable as per norms. | Letter written for insufficient 213/08.01.2026 | Godhra | Halol | Halol R
27 | Cow,Tanki Ni Pase,Vill-Modhala,Tal-Naswadi,Dist-Chhotaudepur | 2025-12-26 | FA | [5 empty] | As Per Site Visit And Statement Of Eye Witness And Owner It Is Came To Know That Cow Was Grassing and passing near 100 KVA Transformer Structure of pain in tank , meanwhile momentarily leakage current passed in earthing wire of that transformer structure. Due to water logging near the transformer may be momentarily leakage occurred and the cow may be pass so died at the same time due to electrocuted. | [6 empty] | Awaited | NA | NA | Earthing Reactivated, PVC Pipe Provided | 15000 under Process | Baroda (O & M) | Bodeli | Naswadi
28 | Amitbhai Jayantibhai Baria (EA),Opp Paramhitdham Aashram,Vill-Mandva,Tal-Dabhoi,Dist-Vadodara | 2025-12-27 | NFHD | [5 empty] | 11 KV NanderiyaAG feeder line clear permit had been taken by him, while the other feeder had not taken the line permit of 11 kv Mota Karara AG. when Mr. Amit Bariya climbed the pole with the alluminume ring which was worn on his shoulder after taking the LC. Alluminiume ring was unfortunately touched on stand by power of 11kv Motakarara AG feeder and he got electrocuted by coming into contact with the live line of 11kv Mota Karara AG and fall down from pole. | [6 empty] | Awaited /L.NO CHD/T/1363 & DT:29-12-2025 | NA | NA | 1 Nos New Rsj Pole erected in place of Psc shackle Pole & change Over HT supply cut off from NEARER TO TCDP | N.A | Baroda (O & M) | Dabhoi | Chhandod

## MG SoP 03B
SOP 3-00B - REGISTER FOR COMPILING THE COMPLAINTS - CLASSIFIFCATION WISE
Quarter of the year : Q-III (Oct-Nov-Dec-2025)
Name of Office : MGVCL Corporate Office
Classification | Nature of Complaints | Pending complaints of previous qtr. | Complaints received during the qtr. | Total Complaints | No. of Complaints redressed during the quarter. |  |  | Balance Complaints to be redressed
[5 empty] | Within stipulated time. | Beyond stipulated time. | Total
| 1 | 2 | 3 | 4=2+3 | 5 | 6 | 7=5+6 | 8=4-7
A | Interruption in power supply | 0 | 192642 | 192642 | 192642 | 0 | 192642 | 0
I | Loose connections at meter, MCB or service line or from pole | 0 | 83188 | 83188 | 83188 | 0 | 83188 | 0
II | Interruption due to line breakdown | 0 | 54475 | 54475 | 54475 | 0 | 54475 | 0
III | No power complaint on account of blowing of HT/ DropOut (DO)/ LT fuse | 0 | 41706 | 41706 | 41706 | 0 | 41706 | 0
IV | Interruption due to failure of transformer or distribution transformer MCB | 0 | 3309 | 3309 | 3309 | 0 | 3309 | 0
V | Load shedding/ schedule outages | 0 | 9964 | 9964 | 9964 | 0 | 9964 | 0
B | Quality of power supply | 0 | 9308 | 9308 | 9308 | 0 | 9308 | 0
I | Ordinary case, which requires no augmentation, | 0 | 5461 | 5461 | 5461 | 0 | 5461 | 0
II | Where augmentation is required. | 0 | 2036 | 2036 | 2036 | 0 | 2036 | 0
III | Harmonics related issue | 0 | 39 | 39 | 39 | 0 | 39 | 0
IV | Neutral voltage related issue | 0 | 561 | 561 | 561 | 0 | 561 | 0
V | Voltage variations related issue | 0 | 1211 | 1211 | 1211 | 0 | 1211 | 0
C | Meters | 0 | 27898 | 27898 | 27898 | 0 | 27898 | 0
I | Stopped/Defective Meters. | 0 | 14157 | 14157 | 14157 | 0 | 14157 | 0
II | Meter accuracy test (Fast/ Slow | 0 | 1168 | 1168 | 1168 | 0 | 1168 | 0
III | Burnt Meter | 0 | 650 | 650 | 650 | 0 | 650 | 0
IV | Stolen Meter | 0 | 0 | 0 | 0 | 0 | 0 | 0
V | Billing on average basis for more than two hills | 0 | 5197 | 5197 | 5197 | 0 | 5197 | 0
VI | Meter boxes/ metering system | 0 | 6726 | 6726 | 6726 | 0 | 6726 | 0
D | Overhead lines | 0 | 6328 | 6328 | 6328 | 0 | 6328 | 0
I | Loose Wires | 0 | 4778 | 4778 | 4778 | 0 | 4778 | 0
II | Inadequate ground clearance | 0 | 1550 | 1550 | 1550 | 0 | 1550 | 0
E | Bills | 0 | 14695 | 14695 | 14695 | 0 | 14695 | 0
I | For current bills where no additional information is required | 0 | 9425 | 9425 | 9425 | 0 | 9425 | 0
II | Where additional information relating to correctness of reading etc. is required, | 0 | 4236 | 4236 | 4236 | 0 | 4236 | 0
III | Final bill for vacation of premises/ change of occupancy | 0 | 866 | 866 | 866 | 0 | 866 | 0
IV | Change of Tariff | 0 | 168 | 168 | 168 | 0 | 168 | 0
F | Service connections | 0 | 16692 | 16692 | 16692 | 0 | 16692 | 0
I | Where extension of LT line up to 150 Metre is required | 0 | 4436 | 4436 | 4436 | 0 | 4436 | 0
II | Where extension of LT line of more than 150 Metre and/or augmentation of distribution transformer is required | 0 | 1998 | 1998 | 1998 | 0 | 1998 | 0
III | Where erection of new distribution transformer is required | 0 | 2060 | 2060 | 2060 | 0 | 2060 | 0
IV | Where erection of new HT line and distribution transformer is required and/ or existing HT line network is required to be augmented. | 0 | 2337 | 2337 | 2337 | 0 | 2337 | 0
V | Where EHT level line and/ or Sub-station is required to be erected and/ or augmented | 0 | 4 | 4 | 4 | 0 | 4 | 0
VI | Modification in connected load | 0 | 1740 | 1740 | 1740 | 0 | 1740 | 0
VII | Name change/reconnection/ change of category | 0 | 4011 | 4011 | 4011 | 0 | 4011 | 0
VIII | In case connection is denied after payment against demand note | 0 | 48 | 48 | 48 | 0 | 48 | 0
IX | Transfer of connection | 0 | 58 | 58 | 58 | 0 | 58 | 0
G | Request for reconnection/ consumer wanting disconnection | 0 | 6066 | 6066 | 6066 | 0 | 6066 | 0
H | Refund of amount due in regard to temporary connection | 0 | 847 | 847 | 847 | 0 | 847 | 0
I | Street Light complaint | 0 | 939 | 939 | 939 | 0 | 939 | 0
J | Others | 0 | 21838 | 21838 | 21838 | 0 | 21838 | 0
TOTAL |  | 0 | 297253 | 297253 | 297253 | 0 | 297253 | 0
The format is to be sent quarterly The quarterly reporting of the year means reporting for the period 1st Quarter as Apr-Jun, 2nd Quarter as Jul-Sep, 3rd Quarter as Oct – Dec and 4th Quarter as Jan - Mar of the financial Year. For any other complaints not mentioned in the classification, the sequence for J can be used.

## MG SoP 04
Name of Distribution Licensee: M.G.V.C.L.
Quarter of the year : Q-III (Oct-Nov-Dec-2025)
Year: 2025-26
Performa SoP 004 : Publicity carried out while displaying the contact details of consumer complaints centers.
Particulars should also cover the details of publication of “Manual of Practice for Handling Complaint/ Consumer Charter/ Complaint Charter”, consumer awareness program conducted, advertisement done through various media like TV, newspaper, radio, pamphlets & booklet distributions, Displays etc. The development of website and any medium through which public education is carried out can be included.
Sr. No. (1) | Actions or steps carried out by distribution licensee towards public awareness in the quarter (2) | Likely number of consumers influenced (3) | Details about Media (4)
the Media
1 | RTI Officers Name is displayed at customer care centre on each office | 3740194 | -
2 | Necessary information regarding time schedule for new connection and solving complaints is display on the board. | 3740194 | -
3 | Contact nos. of various officers of the company for emergency contact is also displayed at customer care centre. | 3740194 | Website/ News paper
4 | Safety Meeting with Line Staff at various S/dn,Divisions on Every Monday (Line staff influenced) | 27523 | Meeting/ line staff infulenced
The format is to be sent quarterly. The column 2 shall depict any steps taken by licensee in direction of consumer awareness and educating the consumer through conducting of seminars, meetings, distribution of pamphlets, through guidelines placed on website, formulating team that visit rural area educating consumers on billing, safety measures and procedures for grievance redressal, etc. The quarterly reporting of the year means reporting for the period 1st Quarter as Apr – Jun, 2nd Quarter as Jul – Sep, 3rd Quarter as Oct – Dec and 4th Quarter as Jan – Mar of the financial year.

## MG SoP - 05
Name of Distribution Licensee: M G V C L
Financial Year: 2025-26
Quarter : Q-III (Oct-25 TO Dec-25)
Performa SoP 005: Failure of Distribution Transformer
Sr. No. | Name of Circle | Nos. of existing Distribution Transformers at the start of the quarter | Nos. of Distribution Transformers added during the quarter | Total number of Distribution Transformers on end of quarter | Total number of Distribution transformer failed during quarter | % failure rate of Distribution transformer
|  | A | B | C=A+B | D | H = (D)*100/C
1 | Baroda O&M | 66874 | 1756 | 68630 | 1560 | 2.2731
2 | Baroda City | 11748 | 171 | 11919 | 20 | 0.1678
3 | Anand | 29260 | 470 | 29730 | 305 | 1.0259
4 | Nadiad | 38168 | 787 | 38955 | 381 | 0.97805
5 | Godhra | 71120 | 1306 | 72426 | 1429 | 1.973
| MGVCL | 217170 | 4490 | 221660 | 3695 | 1.667

## SoP007
Name of Distribution Licensee: M G V C L
Financial Year: 2025-26
Quarter : Q-III (Oct-25 TO Dec-25)
Performa SoP 007: Sample Test result for Neutral Voltage
Compliance Sample Test Report for Neutral Voltage
-1 | -2 | -3 | -4 | -5 | -6
Sr. No | Category of consumers | Sample Size | Standard specified in regulation | Deviation of results from the sample test (Numbers) | % age compliance
|  | (Numbers) |  |  | (6) = (5)*100/(3)
| LT consumers | 1441 | 2% | 0 | 0
1 | Domestic | 1023 | 2% | 0 | 0
2 | Commercial | 242 | 2% | 0 | 0
3 | Industrial | 23 | 2% | 0 | 0
4 | Agricultural | 143 | 2% | 0 | 0
5 | Public water works | 10 | 2% | 0 | 0
| HT consumers |  | 2%
6 | HT industrial | 5 | 2% | 0 | 0

## SoP008
Name of Distribution Licensee: M G V C L
Financial Year: 2025-26
Quarter : Q-III (Oct-25 TO Dec-25)
Performa SoP 008: Sample Test result for Voltage variations
Compliance Sample Test Report for voltage variations
-1 | -2 | -3 | -4 | -5
Voltage Level | Sample Size (numbers) | Limit or prescribed standard | Deviation of results from the sample test (Numbers) | % age compliance
(5) = (4)*100/(2)
Low Voltage | 56 | +6% to -6% | 0 | 0
High Voltage | 24 | +6% to -9% | 0 | 0
Extra High Voltage | 1 | +10% to -12.50% | 0 | 0

## SoP009
Name of Distribution Licensee: M G V C L
Financial Year: 2025-26
Quarter : Q-III (Oct-25 TO Dec-25)
Performa SoP 009: Sample Test result for Harmonics
Compliance Sample Test Report for Harmonics
-1 | -2 | -3 | -4 | -5 | -6
Sr. No | Category of consumers | Sample size (Numbers) | Limit or standard prescribed | Deviation of results from the sample test (Numbers) | %age compliance
(6) = (5)*100/(3)
1 | LT consumers | 33 | 3.5% | 0 | 0
2 | HT consumers | 4 | 3% | 0 | 0
3 | EHT consumers | 1 | 3% | 0 | 0
Note: The licensee shall also submit along with the above harmonic data, the records of customer wise drawls of harmonic currents measured at various strategic points.
The formats SoP 008, SoP 009 and SoP 010 have to be sent annually.
For the purpose of annual submissions, the year end has to be considered as the end of December month of a particular year.

## 010
Q-III (Oct-Dec 2025)
Year: 2025-26
SoP 010 – A System Average Interruption Frequency Index (SAIFI)
Sr. No | Month | Number of Sustained Interruptions during the Reporting Period = Ai | Number of Interrupted Customers for Sustained Interruption events during the Reporting Period = Ni | Total number of Customers Served for the Areas = Nt | Total Number of Interrupted Customers for Sustained Interruption events during the Reporting Period = Σ (Ai x Ni) | SAIFI = Σ (Ai x Ni) /Nt
1 | 2 | 3 | 4 | 5 | 6 = Σ (3 x 4) | 7 = 6 / 5
1 | 2025-10-01 | 36670 | 3232891 | 3699822 | 43186436 | 11.67
2 | 2025-11-01 | 26682 | 3058605 | 3681786 | 30478047 | 8.28
3 | 2025-12-01 | 22868 | 3045508 | 3715599 | 26827758 | 7.22
|  | 86220 | 9337004 | 11097207 | 100492241 | 9.0556

## 011
Q-III (Oct-Dec 2025)
Year: 2025-26
SoP 011 – System Average Interruption Duration Index (SAIDI)
Sr. No | Month | Number of Sustained Interruptions during the Reporting Period = Ai (Nos) | Total Outage Duration (Hr : Min) | Restoration time for each Interruption Event = Ri (Hr : Min) | Number of Interrupted Customers for Sustained Interruption events during the Reporting Period = Ni (Nos) | Total Customer Interruption Duration = Ri x Ni (Hr : Min) | Total Number of Customers Served for the Areas = Nt (Nos) | Cumulative Customer Interruptions Duration = Σ(Ri x Ni) (Hr : Min) | SAIDI = Σ (Ri x Ni) / Nt (Hr : Min)
1 | 2 | 3 | 4 | 5 = 4 / 3 | 6 | 7 = 5 x 6 | 8 | 9 = Σ (5 x 6) | 10 = 9 /8
1 | 2025-10-01 | 36670 | 16785:22 | 0:27 | 3232891 | 1454800:57 | 3699822 | 1307912:13 | 0:21
2 | 2025-11-01 | 26682 | 12865:47 | 0:29 | 3058605 | 1478325:45 | 3681786 | 1277446:39 | 0:21
3 | 2025-12-01 | 22868 | 10732:42 | 0:28 | 3045508 | 1421237:04 | 3715599 | 1210093:15 | 0:20
|  | 86220 | 40383:51 | 1:24 | 9337004 | 4833471:13 | 11097207 | 4333028:57 | 0:21

## 012
Q-III (Oct-Dec 2025)
Year: 2025-26
SoP 012 – : Momentary Average Interruption Frequency Index (MAIFI)
Sr. No | Month | Total Number of Momentary interruptions = Imi | Total Number of Consumers affected due to Momentary Interruption Events during the Reporting Period = Nmi | Number of Customer Momentary Interruptions = IMi * Nmi | Total Number of Customers Served for the Areas = Nt | Cumulative Momentary Customer Interruptions = Σ (Imi x Nmi) | MAIFI = Σ (IMi x Nmi)/ Nt
1 | 2 | 3 | 4 | 5=3*4 | 6 | 7 = Σ (3 x 4) | 8=7/6
1 | 2025-10-01 | 53027 | 3012499 | 164636082849 | 3699822 | 71394859 | 19.3
2 | 2025-11-01 | 60621 | 2823385 | 119878103715 | 3681786 | 52659883 | 14.3
3 | 2025-12-01 | 53327 | 2844985 | 106903156360 | 3715599 | 47529426 | 12.79
|  | 166975 | 8680869 | 391417342924 | 11097213 | 171584168 | 15.4619

## 013
Q-III (Oct-Dec 2025)
Year: 2025-26
SoP 013 – : Customer Average Interruption Duration Index (CAIDI)
Sr. No | Month | Total Number of Sustained Interruptions during the Reporting Period = Σ Ai | Total Restoration time for Interruption Events = Σ Ri (Hr : Min) | Total Number of Interrupted Customers for Sustained Interruption events during the Reporting Period = Σni | CAIDI=Σ (Ri x Ni) / Σ (Ai x Ni) = SAIDI/ SAIFI
1 | 2 | 3 | 4 | 5 | 6 = (4 x 5) / (3 x 5)
1 | 2025-10-01 | 36670 | 0:27 | 3232891 | 1.8
2 | 2025-11-01 | 26682 | 0:28 | 3058605 | 2.54
3 | 2025-12-01 | 22868 | 0:28 | 3045508 | 2.77
|  | 86220 | 1:23 | 9337004 | 2.37

## MG SoP - 15
Name of Distribution Licensee: M G V C L
Financial Year: 2025-26
Quarter : Q-III (Oct-25 TO Dec-25)
Performa SoP 015: Faulty Meters Replacement
Consumer Category | No. of faulty meters at the start of the quarter | No. of faulty meters added during the quarter | Total no. of defective / faulty Meter | No. of faulty Meters repaired and replaced | No of faulty meters pending at the end of the quarter | Remark
| 1 | 2 | (3)=(2)+(1) | 4 | (5)=(3)-(4)
Single Phase | 6508 | 38615 | 45123 | 35009 | 10114
Three Phase | 4380 | 6867 | 11247 | 6527 | 4720

## MG SoP 16
Name of Distribution Licensee: M G V C L
Financial Year: 2025-26
Quarter : Q-III (Oct-25 TO Dec-25)
Performa SoP 016: Compensation details
COMPENSATION DETAILS
Sr. No. | Service Area | Compensation payable to | Claimed |  | Payable
|  | consumer for the period of default in case of violation of standard | No. of cases | Amount (Rs.) | No. of cases in which compensation is payable | Amount payable (Rs.) | Amount paid (Rs.)
1 | Registration of complaint and intimation of Unique complaint Number to the Complainant | Rs. 50/- for each default | 0 | 0 | 0 | 0 | 0
2 | Issuance of Demand Note for New Connection, Load Enhancement, Shifting of connection at other premises, Conversion of Service, Temporary Supply, Shifting of Service Connection in exiting premises, Deviation of line and Shifting of equipments | Rs. 50 for each day of default. | 0 | 0 | 0 | 0 | 0
3 | New Connection, Load Enhancement, Shifting of connection at other premises and Conversion of Service where no Network erection and/or augmentation is required. | Rs. 50 for each day of default. | 0 | 0 | 0 | 0 | 0
4 | New Connection, Load Enhancement, Shifting of connection at other premises and Conversion of Service where Network erection and/or augmentation is required. | Rs. 50 for each day of default. | 0 | 0 | 0 | 0 | 0
5 | Release of temporary supply | Rs. 50 for each day of default. | 0 | 0 | 0 | 0 | 0
6 | Shifting of meter/services in the existing premises | Rs. 50 for each day of default. | 0 | 0 | 0 | 0 | 0
7 | Shifting of LT/HT lines |  | 0 | 0 | 0 | 0 | 0
8 | Shifting of Transformer structures |  | 0 | 0 | 0 | 0 | 0
9 | Settlement of amount for refunding of excess amount after completion of work. |  | 0 | 0 | 0 | 0 | 0
10 | Transfer of Service Connection with respect to change of name or change of ownership | Rs. 50 for each day of default. | 0 | 0 | 0 | 0 | 0
11 | Application from consumer requesting Change in Tariff Class/Category. | Rs. 50 for each day of default. | 0 | 0 | 0 | 0 | 0
12 | Complaint Related to Billing | Rs. 50 for each day of default. | 0 | 0 | 0 | 0 | 0
13 | Replacement of Meter | Rs. 25/- for each day of default subject to maximum of Rs. 1500/- for LT connections and Rs. 250/- for each day of default subject to maximum of Rs. 2500/- for HT connections. | 0 | 0 | 0 | 0 | 0
14 | Reconnection of Supply | Rs. 25/- for each six hours (or part thereof) of delay in restoration of supply subject to maximum Rs. 500/- for LT connection and Rs. 50/- for each six hours (or part thereof) of delay in restoration of supply subject to maximum Rs. 1000/- for HT connection. | 0 | 0 | 0 | 0 | 0
15 | More than 2 interruptions in a day to the consumer for the reasons not attributable to the nature of fault as mentioned in Clause 8.4 of these Regulations. | Rs. 25/- for each interruption subject to maximum Rs. 500/- for LT connection and Rs. 50/- for each interruption subject to maximum Rs. 1000/- for HT connection. | 0 | 0 | 0 | 0 | 0
16 | Failure to restore power supply in case of blowing of fuse of LT side distribution transformer, at consumer premises, trouble of MCB of distribution transformer, loose connection at pole, MCB or meter, etc. | Rs. 50/- per hour per Consumer for the first two hours of default. Thereafter Rs. 100/- per hour per Consumer subject to maximum of Rs. 500/- per day for LT consumer and maximum of Rs. 2000/- per day for HT consumer. | 0 | 0 | 0 | 0 | 0
17 | Failure to restore power supply in case of blowing of HT side fuse of distribution transformer |  | 0 | 0 | 0 | 0 | 0
18 | Failure to restore power supply in case of HT and LT line fault |  | 0 | 0 | 0 | 0 | 0
19 | Failure to restore power supply in case of Distribution transformer failure |  | 0 | 0 | 0 | 0 | 0
20 | Failure to restore power supply in case of failure of underground service or underground HT/LT cable |  | 0 | 0 | 0 | 0 | 0
21 | Scheduled Power Outage | Rs. 50/- per hour per Consumer for the first two hours of default. Thereafter Rs. 100/- per hour per Consumer | 0 | 0 | 0 | 0 | 0
22 | Site Visit and Intimation to the Consumer about likely time to resolve the complaint related to voltage fluctuation. | Rs. 200/- for each instance for each complaint. | 0 | 0 | 0 | 0 | 0
23 | Complaint of Neutral Voltage | Rs. 250/- for each complaint | 0 | 0 | 0 | 0 | 0
24 | Complaint regarding Voltage variations at the point of commencement of supply. | Rs. 25/- for each day of default subject to maximum of Rs. 500/- | 0 | 0 | 0 | 0 | 0

## MG SoP 17
Performa SoP 017: Individual Complaint where Compensation has been paid (To be submitted Quarterly)
Sr. No. | Complaint No. | Date of filing Complaint/ Automatic Compensation | Consumer No. and Name and Address of the Consumer | Nature of Complaint | Reference Standard of Performance | Amount of compensation (Rs.) | Whether Compensation paid automatically or Consumer has to approach CGRF to get compensation | Whether CGRF has upheld demand of Consumer of Compensation and if Yes, date of order of CGRF and date of compensation paid
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## SOP 18
1. Unauthorised use of Electricity (3rd Quarter as Oct 25 - Dec 25)
No. of cases Booked | No. of cases where UUE is established by the Licensee | No. of cases where appeal filed by the consumer before the Apellate Authority | No. of cases decided by the Appellate Authority in favour of the the Licensee | No. of cases decided by the Appellate Authority in favour of the the Consumer
492 | 492 | 0 | 0 | 0
226 | 226 | 0 | 0 | 0
179 | 179 | 0 | 0 | 0
196 | 196 | 0 | 0 | 0
562 | 562 | 0 | 0 | 0
1655 | 1655 | 0 | 0 | 0
Note:- | The format is to be sent quarterly.
The format shall include individual consumer wise details.
The quarterly reporting of the year means reporting for the period 1st Quarter as Apr – Jun, 2nd Quarter as Jul – Sep, 3 rd Quarter as Oct – Dec and 4th Quarter as Jan – Mar of the financial year.

## SOP 19
2. Theft of Electricity (3rd Quarter as Oct 25 - Dec 25)
No. of cases Booked | No. of complaints filed by the Licensee in Police Station | No. of cases in which the judgement delivered by the Special Court | No. of cases decided by the Special Court in favour of Licensee | No. of cases decided by the Special Court in favour of Consumer
1201 | 1201 | 0 | 0 | 0
210 | 210 | 0 | 0 | 0
560 | 560 | 0 | 0 | 0
466 | 466 | 0 | 0 | 0
3176 | 3176 | 0 | 0 | 0
5613 | 5613 | 0 | 0 | 0
Note:- | The format is to be sent quarterly.
The format shall include individual consumer wise details.
The quarterly reporting of the year means reporting for the period 1st Quarter as Apr – Jun, 2nd Quarter as Jul – Sep, 3 rd Quarter as Oct – Dec and 4th Quarter as Jan – Mar of the financial year.