## MG COVER PAGE
Name of Distribution Licensee: M G V C L
Quarter : Q-IV (Jan-Feb-Mar-2022-23)
Year: 2022-23

## MG SoP 01
Name of Distribution Licensee: M G V C L
Quarter IV (Jan-23 to Mar-23)
Year:2022-23
Performa - SoP 001: Fatal and Non-fatal accident report
NUMBER OF ACCIDENTS FOR THE FOURTH QUARTER 2022-23
Sr. No | Name of Area/Circle | No of accidents in the quarter |  |  |  |  | Cumulative since the first quarter of the current FY year |  |  |  |  | Cumulative since the first quarter of the Last FY 2021-22
|  | Departmental |  | Outside |  |  | Departmental |  | Outside |  |  | Departmental |  | Outside
|  | FH | NFH | FH | FA | NFH | FH | NFH | FH | FA | NFH | FH | NFH | FH | FA | NFH
1 | Baroda City | 0 | 1 | 0 | 0 | 0 | 0 | 3 | 1 | 0 | 0 | 0 | 1 | 1 | 4 | 0
2 | Baroda (O&M) | 0 | 0 | 4 | 0 | 0 | 0 | 7 | 12 (1-Pvt) | 19 | 4 | 0 | 4 | 8 | 26 | 4
3 | Anand | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 3 | 5 | 1 | 1 | 2 | 6 | 11 | 1
4 | Godhra | 0 | 1 | 1 | 1 | 0 | 0 | 3 | 17 (9-Pvt) | 25 (2-Pvt) | 6 | 1 | 1 | 9 (1-Pvt) | 35 | 4 (1-Pvt)
5 | Nadiad | 0 | 1 | 2 | 1 | 2 | 0 | 5 | 11 (2-Pvt) | 23 | 6 | 1 | 2 | 6 | 17 | 1
| TOTAL | 0 | 3 | 8 | 3 | 2 | 0 | 19 | 44 (12-Pvt) | 72 (2-Pvt) | 17 | 3 | 10 | 30 (1-Pvt) | 93 | 10 (1-Pvt)
[6 empty] | 16 |  |  |  |  | 152 |  |  |  |  | 146

## SoP 002
Performa – SoP 003: Action taken report for safety measures complied for the electrical accidents occurred
ACTION TAKEN REPORT FOR SAFETY MEASURES COMPLIED FOR THE ELECTRICAL ACCIDENTS OCCURED IN THE FOURTH QUARTER OF FY 2022-23
1 | 2 |  |  | 3 | 4 |  |  | 5 | 6 | 7 | 8 | 9 | 10
Sr. No | Location of Accident and details of the victim | Address | sdn | Date of occurrence | Type of Accident | Installation | Accident Type | Cause of Accident | Findings of CEI / EI / AEI | Remedies suggested by CEI /EI / AEI in various cases | Whether the remedy suggested is complied | Action taken to avoid recurrence of such Accident | Circle office | Reason
1 | BABUBHAI KALABHAI PARMAR, SIM VISTAR, Vill-DANTALI, Tal-KAPADWANJ, Dist-Kheda |  |  | 2023-01-02 | FHO |  |  | ON DATED 02.01.2023 AROUND 11:30AM VICTIM LATE SHRI BABUBHAI KALABHAI PARMAR & TWO OF HIS RELATIVES 1. ASHWINBHAI BHALABHAI PARMAR 2. VISHALBHAI SHANABHAI PARMAR WERE TRYING TO FIT HIS SUBMERSIBLE MOTOR IN HIS BOREWELL WITH THE HELP OF 2 TYRE VEHICLE(GHODI OR CART) WHICH IS ATTACHED WITH 18.5 FEET LONG IN HEIGHT METAL PIPE. (HEIGHT OF 2 TYRE VEIHCLE (GHODI OR CART) IS 2.6 FEET & PIPE IS 18.5 FEET, SO TOTAL HEIGHT IS MORE THAN 21 FEET). 11KV SUKI AG FDR LINE IS PASSING ABOVE THIS LOCATION. VICTIM | AWAITED | NA | NA | Estimate was issued for Shifting of line | Nadiad | 6
2 | ASHWINBHAI BHALABHAI PARMAR (AGE-35), VISHALBHAI SHANABHAI PARMAR (AGE-27), SIM VISTAR, Vill-DANTALI, Tal-KAPADWANJ, Dist-Kheda |  |  | 2023-01-02 | NFHO |  |  | ON DATED 02.01.2023 AROUND 11:30AM VICTIM LATE SHRI BABUBHAI KALABHAI PARMAR & TWO OF HIS RELATIVES 1. ASHWINBHAI BHALABHAI PARMAR 2. VISHALBHAI SHANABHAI PARMAR WERE TRYING TO FIT HIS SUBMERSIBLE MOTOR IN HIS BOREWELL WITH THE HELP OF 2 TYRE VEHICLE(GHODI OR CART) WHICH IS ATTACHED WITH 18.5 FEET LONG IN HEIGHT METAL PIPE. (HEIGHT OF 2 TYRE VEIHCLE (GHODI OR CART) IS 2.6 FEET & PIPE IS 18.5 FEET, SO TOTAL HEIGHT IS MORE THAN 21 FEET). 11KV SUKI AG FDR LINE IS PASSING ABOVE THIS LOCATION. VICTIM | AWAITED | NA | NA | Estimate was issued for Shifting of line | Nadiad | 6
3 | VALAMBHAI KALABHAI PARMAR, VYAS VASNA SIM,Vill-VYAS VASNA, Taluka:Kapadwanj,District: Kheda |  |  | 2023-01-06 | NFHO |  |  | ON DATED 06.01.2023 AROUND 14:30 HOURS VICTIM SHRI VALAMBHAI KALABHAI PARMAR WAS CUTTING TREE BRANCH FOR FEED THE ANIMAL BY CLIMBING ON THE SECOND HOLE OF PSC POLE OF 11 KV ALWA AG FEEDER.DURING THE CUTTING OF TREE BRANCH(GORAS AMBALI) BY VANSI BY WHICH THE TREE BRANCH CUT,VANSI SUDDENLY COMES IN CONTACH WITH 11 KV LIVE LINE AND BY ELECTRUDE VICTIM FELT DOWN ON THE LAND.AS PER EYE WITNESS SHRI PATEL LALABHAI MOHAN BHAI VICTIM WAS TAKEN TO NEARBY HOSPITAL BY 108 . | AWAITED | NA | NA | Public Awarenss program for safety awareness were exacuted | Nadiad | 6
4 | MAHENDRABHAI RAJESHBHAI GUPTA, SANKARDA BHADARWA ROAD,Vill-Moxi, Tal-Savli, Dist-vadodara |  |  | 2023-01-06 | FHO |  |  | DUE TO ONGOING WORK OF ROAD WIDENING AND NEW ROAD OF SANKARDA-BHADARWA BY R&B DEPARTMENT. THEY WERE CARRIED OUT ROAD WIDENING WORK AND FILLING BESIDES LAND AND DRAINAGE WITH SANDS AND STONE CHIPS. DUE TO THE FILLING, GROUND CLEARANCE OF 11 KV LINE REDUCED. THE EICHER DRIVER TOOK VEHICLE UNDER-CONSTRUCTION BESIDE ROAD AND DUE TO EICHER VEHICLE HIGHT EXTENSION BY ADDITIONAL FABRICATION IT CAME IN CONTACT WITH LINE 11 KV CONDUCTOR. SO 11 KV ELECTRIC SUPPLY CONTINUES FLEW THROUGH EICHER AND EICHER | Awaited | NA | NA | psc pole replaced with 11 Meter girder pole and incerase the line clearance | Baroda O&M | 6
5 | BHARWAD VANRAJBHAI RAJABHAI,FARM OF BHARWAD RUPABHAI,B/H ONGC WELL NO.1,JUNI AKHOL ROAD,Vill-LUNEJ, Tal-Khambhat, Dist-Anand |  |  | 2023-01-08 | FHO |  |  | On receipt of telephonic information to concern onduty staff by Sarpanch shree ,Lunej ,Dated 08.01.23 @11.45, During visit at site on Dtd 08.01.23,it is found that the accident took place on the 11KV Gudel JGY feeder at DP Structure of rail pole having GEO location No.38/29,Due to Some unknown reason the top conductor opened from D Jumper from one side but still connected on opposite side of same pole same phase,This results of that conductor span got lossed and produced low ground clearance in | Awaited | NA | NA | girder pole erected & clearance maintained , guarding also provided | Anand | 1
6 | VASAWA SANJAYBHAI BUDHABHAI, Vill-KOLIYAD,Tal-karjan, Dist-Vadodara |  |  | 2023-01-14 | FHO |  |  | On DT:- 14-01-2023, the victim while flying kite on his friend's house terrace ran for catching another kite on terrace of his friend's neighbour house and came in contact with live conductor passing over the house of neighbour staying beside house of victim's friendand hence victim got electrocuted and died on the spot | Awaited | NA | NA | notice issued for illegal construction | Baroda O&M | 2
7 | Kalabhai Gopichandbhai Parmar, BHANPUR TALAV FLY,Vill-BHANPUR, Tal-Dhanpur, Dist-Dahod |  |  | 2023-01-29 | FHO |  |  | As per primary investigation information recieved from Villagers that unauthorise fencing of iron wire surrounding the farm of Shri Makansing Veljibhai Parmar Which was founded by villagers . The electric current fed to that fencing by Farm owner through unauthorise hooking from LT line which is about 700 meter away from incidence place. As per villagers ,The victim may be came in contact with this live fencing of farm and get electric shock and died on the moreover as per information by villa | AWAITED | NA | NA | At the Time Of Investigation SDO MGVCL Garbada On No Victim Dead Body On Incidence Place And No Any Unauthorized Hooking Lunger Wire Was Found On Fencing Of Farm. Local Police Had Done Their Investigation Before Investigation By MGVCL.letter written vide 318/03.02.2023 to dhanpur police station for tempered (direct hooking ) with lt line. | Godhra | 6
8 | COWS OF KALUBHAI HARIBHAI BHARVAD,BHARVAD FLY,Vill-Rabdal, Tal-Dahod, Dist-Dahod |  |  | 2023-01-29 | FA |  |  | According to the information received at complain center by Sh Bharatbhai Kalubhai Bharwad current may be leakaged through kite thread on the pole.The kite thread surrounded the pole and touched LT 2w open conductor and the GI earth wire.Due to the rain the thread got wet and circulating power from lt line to the GI wire.At the bottom of the pole private fancing barbed wire bounded with the pole.The cows touched with the barbed fancing wire and got electrocuted and fell down on the ground and wa | AWAITED | NA | NA | KITE THREAD REMOVED AND INSTRUCT CONCERN TO REMOVE BARBED WIRE OF HIS FANCING FROM THE POLE | Godhra | 2
9 | ZALA DHAMAJI GOTAJI, VIRAVAT NI MUVADI, Vill-RANODARA, Tal-Daskoi, Distt-Ahmedabad |  |  | 2023-02-09 | FA |  |  | 3 PH 4 WIRE AG LT OF 11 KV HATHNOLI AG FDR PASSING THROUGH THE PREMISES OF ZALA DHAMAJI GOTAJI, AT LOC. VIRAVAT NI MUVADI. VILL: RANODARA FOR 3 PH-AG CONN OF ZALA GALAJI BADHAJI. THIS LT LINE IS VERY OLD 3 PH 5 WIRE AAAC 34 SQMM. IN THE MORNING FROM THIS 3 PH 4 WIRE AAAC 34 SQMM ONE TOP CONDUCTOR BROKEN AND FALL DOWN TO THIS BUFFALO. SO THIS BUFFALO MEET THE ELECTRICAL ACCIDENT AND DIED ON SAME PLACE. | AWAITED | NA | NA | DETERIORATED CONDUCTOR CHANGE AT THE ACCIDENT PLACE | Nadiad | 1
10 | RAMESHBHAI DINESHBHAI CHAUHAN, Vill-Balol, Tal-Mahudha, Distt-Kheda |  |  | 2023-02-11 | FHO |  |  | As per eye witness statement the victim was working for digging well(khalkuvo) in the farm. Victim was put an iron rod to measure the depth of the well.While he raised an iron rod,iron rod was accidentally touch the live wire of 11 kv Kaprupur ag dom feeder which passing through the farm above the well. So the victim came in contact with the live wire and hence got electrocuted. | AWAITED | NA | NA | Awareness given | Nadiad | 6
11 | Chakiben Teriyabhai Rathwa, near APMC, Vill-Chhotaudepur, Tal/Distt-Chhotaudepur |  |  | 2023-02-12 | FHO |  |  | As per primary investigation information recieved from villagers that victim(labor) climbed on iron roof to remove one iron roof which is obstacles in manufacturing of civil column. accidently she contact in one live conductor of 11kv feeder, electrocuted & died on the spot. | Awaited | NA | NA | No action required | Baroda O&M | 6
12 | Vishalkumar Rameshbhai Bhoi, Atlantis K 10 Building, Vadodara |  |  | 2023-02-17 | NFHD |  |  | DURING ROUTINE DC ACTIVITY WORK AT ALKAPURI SDN SHRI. VISHAL R. BHOI AGE 23 APPROX. WORKING AS EA- VS ALONG WITH SHRI. D. B. RATHOD EA HAS GONE FOR DC WORK AT SARABHAI CAMPUS AREA AT ATLANTIS K-10 COMPLEX-.DURING THE DISCONNECTION SHRI. VISHALKUMAR BHOI NOT HAVE IDENTIFIED THE MAIN SUPPLY WIRES AND BY MISTAKE HE MAY CAME IN CONTACT TO MAIN SUPPLY INSTEAD OF LOAD SIDE THAT HAVE CAUSED ARC AND FLASHES WHICH HAS RESULTED IN THE INJURIES IN THE HANDS OF VISHAL BHOI. | AWAITED | NA | NA | Awereness givin to victim & co-workers to adopt safe practices during work | Baroda City | 3
13 | K.C. Damor, Veerakuva sim vistar, Vill-Khijalpur vanto, Tal-Thasara, Distt-Kheda |  |  | 2023-02-23 | NFHD |  |  | There was complaint of AG consumer for jumper burnt, during petrolling he found incoming Y phase tapping DODP DO fuse was burnt of Veerakuva AG feeder, So he isolated AB s/w and tried to climb without local earthing, he also forgotten due to U/G cable kit failure at Umreth SS, Veerakuva AG feeder getting power from Khijalpur AG feeder Change over. due to this he isolated wrong AB s/w, live line and got electricuted. | Awaited | Awaited | No | 11 KV Cable kit of Veerakuva Ag feeder was fired on Dated 20.02.2023 ,Newe 11 KV Cable Kit was provided on dated 21.02.2023. Power was restored on 11 Veerakuva feedr on dated 27.02.2023 from Khijalpur AG feeder | Nadiad | 3
14 | SH. RIMJIBHAI JOGIBHAI RATHWA,Vill-PANIBAR, Tal-PAVI JETPUR, Dist-Chhotaudepur |  |  | 2023-03-09 | FHO |  |  | ON DT. 09.03.23 SH. RIMJIBHAI JOGIBHAI RATHWA WAS ERECTING AN UNAUTHORIZED POLE OF ‘MANDAP’ UNDER EXISTING 11 KV OH HT LINE OF 11 KV BHINDOL JGY FEEDER AT PANIBAR VILLAGE. WHILE HANDLING THE POLE, IT ACCIDENTLY CAME IN CONTACT WITH THE LIVE OH HT LINE CONDUCTOR & THE VICTIM GOT ELECTROCUTED. | Awaited | NA | NA | No action required | Baroda O&M | 6
15 | DINESH R CHAUHAN,IDGAH MOHHALA,Vill-GODHRA, Tal-GODHRA, Dist-PANCHMAHAL |  |  | 2023-03-22 | NFHD |  |  | After disconnecting the supply from TC, Shri D R Chauhan (victim) & Shri S N Asari were carrying out the LT Jumpering work , suddenly Return power came on LT line and Shri D R Chauhan experienced electric shock in hand & got unbalanced from the pole and fall on Ground .The victim Shri D R Chauhan have an injury on forehead and left leg knee.He immediately shifted to private hospital at Godhra for treatment and from there he shifted to Zydus hospital at Anand. | AWAITED | NA | NA | Awareness given | GODHRA | 3
16 | BUFFALO,TEKRA FALIYU,Vill-VATAV, Tal-PETLAD, Dist-ANAND |  |  | 2023-03-23 | FA |  |  | DUE TO HEAVY WIND AND RAIN, DROPPER WIRE USED FOR LT CONNECTION ACCIDENTLY TOUCHED WITH EARTH GI WIRE OF POLE EARTHING AND CURRENT FLOW THROUGH GI EARTH WIRE, HENCE BUFFALO ELECTOCUTED AND DEAD. | Awaited | NA | NA | remove GI wire from droper joint & insulated tap provded | Anand | 2

## MG SoP 03B
Name of Distribution Licensee: M G V C L
Quarter : Q-IV (Jan-Feb-Mar-2022-23)
Year: 2022-23
REGISTER FOR COMPILING THE COMPLAINTS CLASSIFICATIONWISE Q-I 2023
Performa SoP 003 B: |  |  |  | APPENDIX-B (already in the SoP regulation)
Classification | Nature of Complaints | Pending complaints of previous qtr. | Complaints received during the qtr. | Total Complaints =2+3 | No. of Complaints redressed during the quarter. |  |  |  |  | Balance Complaints to be redressed. (4) – (9)
[5 empty] | In stipulated time |  | Beyond stipulated time |  | Total (5) to (8)
[5 empty] | Within 50% of stipulated time. | Within stipulated time. | Up to double the stipulated time | More than double the stipulated time
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
A(i) | Loose Connection | 0 | 60209 | 60209 | 30322 | 29887 | 0 | 0 | 60209 | 0
A(ii) | Intruption due to line Break down | 0 | 41447 | 41447 | 19299 | 22148 | 0 | 0 | 41447 | 0
A(iii) | Intruption due to T/C Fail | 0 | 5252 | 5252 | 2880 | 2372 | 0 | 0 | 5252 | 0
B(i) | Quality of power supply,ordinary case which require no Augmentation | 0 | 7556 | 7556 | 4872 | 2684 | 0 | 0 | 7556 | 0
B(ii) | Quality of power supply,ordinary case which require Augmentation | 0 | 4017 | 4017 | 2034 | 1983 | 0 | 0 | 4017 | 0
C(i) | Meters- Stoped/Defective meter | 0 | 13847 | 13847 | 8667 | 5180 | 0 | 0 | 13847 | 0
C(ii) | Meters- Billing on average basis for > two bills | 0 | 5388 | 5388 | 3235 | 2153 | 0 | 0 | 5388 | 0
D(i) | Over head lines - loose wires | 0 | 4717 | 4717 | 2327 | 2390 | 0 | 0 | 4717 | 0
D(ii) | Over head lines - in adiquate ground clearance | 0 | 930 | 930 | 463 | 467 | 0 | 0 | 930 | 0
E(i) | Bills- for current bills where no addl information required | 0 | 3262 | 3262 | 2212 | 1050 | 0 | 0 | 3262 | 0
E(ii) | Bills- for current bills where addl information required | 0 | 2559 | 2559 | 1192 | 1367 | 0 | 0 | 2559 | 0
F(i) | Service connections- where extention of mains is not required | 0 | 6508 | 6508 | 4643 | 1865 | 0 | 0 | 6508 | 0
F(ii) | Service connections- where extention of mains is required | 0 | 3129 | 3129 | 1459 | 1670 | 0 | 0 | 3129 | 0
F(iii) | Service connections- Modification in connected load | 0 | 2871 | 2871 | 1120 | 1751 | 0 | 0 | 2871 | 0
F(iv) | Service connections- Name change/reconnection | 0 | 3031 | 3031 | 1417 | 1614 | 0 | 0 | 3031 | 0
G | Refund of amount due inregard to temp conn | 0 | 453 | 453 | 203 | 250 | 0 | 0 | 453 | 0
H | Others | 0 | 20422 | 20422 | 9999 | 10423 | 0 | 0 | 20422 | 0
| TOTAL | 0 | 185598 | 185598 | 96344 | 89254 | 0 | 0 | 185598 | 0

## MG SoP 04
Name of Distribution Licensee: M G V C L
Quarter : Q-IV (Jan-Feb-Mar-2022-23)
Year: 2022-23
Performa SoP 004 : Publicity carried out while displaying the contact details of consumer complaints centers
Particulars should also cover the details of consumer awareness program conducted, advertisement done through various media like TV, newspaper, radio, pamphlets & booklet distributions, Displays etc. The development of website and any medium through which public education is carried out can be included.
Sr. No | Actions or steps carried out by distribution licensee towards public awareness in the quarter | Likely number of consumers influenced
1 | RTI Officers Name is displayed at customer care centre on each office | 3487443
2 | Necessary information regarding time schedule for new connection and solving complaints is display on the board. | 3487443
3 | Contact nos. of various officers of the company for emergency contact is also displayed at customer care centre. | 3487443
4 | Displayed safety posters at various S/dn,Divisions | 4800
5 | Safety Meeting with Line Staff at various S/dn,Divisions on Every Monday (Line staff influenced) | 3605

## SOP-05
Name of Distribution Licensee: M G V C L
SOP Q-IV
Year :2022-23
Performa – SoP 005 B: Action taken report by the Redressal Committee
Sr. No | Month | Date and Time Meeting conducted | No of complaints registered at the meeting | No. of complaints pending at the end of the meeting
1 | 1st Month of the quarter (Jan-23) | NIL | NIL | NIL
2 | 2nd Month of the quarter (Feb23) | NIL | NIL | NIL
3 | 3rd Month of the quarter (March23) | 28.03.23 11:30 AM at corporate office vadodara | 8 | 0

## MG SoP - 06
Name of Distribution Licensee: M G V C L
Financial Year: 2022-23
Quarter : Q-IV (Jan-Feb-Mar-2023)
Performa SoP 006: Failure of Distribution Transformer
Sr. No. | Name of Circle | Nos. of existing Distribution Transformers at the start of the quarter | Nos. of Distribution Transformers added during the quarter | Total number of Distribution Transformers on end of quarter | Total number of Distribution transformer failed during quarter-IV | % failure rate of Distribution transformer
|  | A | B | C=A+B | D | H = (D)*100/C
1 | Baroda O&M | 53982 | 2797 | 56779 | 588 | 1.0356
2 | Baroda City | 9368 | 135 | 9503 | 9 | 0.094707
3 | Anand | 24872 | 444 | 25316 | 133 | 0.52536
4 | Nadiad | 31870 | 1035 | 32905 | 221 | 0.67163
5 | Godhra | 60881 | 1006 | 61887 | 724 | 1.1699
| MGVCL | 180973 | 5417 | 186390 | 1675 | 0.89865

## SoP008
Name of Distribution Licensee: M G V C L
Quarter : Q-4 (Jan-Feb-March- 2023)
Year: 2022-23
Performa SoP 008: Sample Test result for Neutral Voltage
Compliance Sample Test Report for Neutral Voltage
-1 | -2 | -3 | -4 | -5 | -6
Sr. No | Category of consumers | Sample Size | Standard specified in regulation | Deviation of results from the sample test (Numbers) | % age compliance
|  | (Numbers) |  |  | (6) = (5)*100/(3)
| LT consumers | 1441 | 2% | 0 | 0
1 | Domestic | 1023 | 2% | 0 | 0
2 | Commercial | 242 | 2% | 0 | 0
3 | Industrial | 23 | 2% | 0 | 0
4 | Agricultural | 143 | 2% | 0 | 0
5 | Public water works | 10 | 2% | 0 | 0
| HT consumers |  | 2%
6 | HT industrial | 5 | 2% | 0 | 0

## SoP009
Name of Distribution Licensee: M G V C L
Quarter : Q-4 (Jan-Feb-March- 2023)
Year: 2022-23
Performa SoP 009: Sample Test result for Voltage variations
Compliance Sample Test Report for voltage variations
-1 | -2 | -3 | -4 | -5
Voltage Level | Sample Size (numbers) | Limit or prescribed standard | Deviation of results from the sample test (Numbers) | % age compliance
(5) = (4)*100/(2)
Low Voltage | 56 | +6% to -6% | 0 | 0
High Voltage | 24 | +6% to -9% | 0 | 0
Extra High Voltage | 1 | +10% to -12.50% | 0 | 0

## SoP010
Name of Distribution Licensee: M G V C L
Quarter : Q-4 (Jan-Feb-March- 2023)
Year: 2022-23
Performa SoP 010: Sample Test result for Harmonics
Compliance Sample Test Report for Harmonics
-1 | -2 | -3 | -4 | -5 | -6
Sr. No | Category of consumers | Sample size (Numbers) | Limit or standard prescribed | Deviation of results from the sample test (Numbers) | %age compliance
(6) = (5)*100/(3)
1 | LT consumers | 33 | 3.5% | 0 | 0
2 | HT consumers | 4 | 3% | 0 | 0
3 | EHT consumers | 1 | 3% | 0 | 0

## 11A
Q-4(Jan-Mar-23)
Year: 2022-23
SoP 011 –A: System Average Interruption Frequency Index (SAIFI)
Sr. No | Month | Ni - Total no of customers for each momentary interruptions | NT - Total no of customers served |  |  | Past year corrosponding Month
1 | 2 | 3 | 4 | 5 | 6=5/4
1 | Jan' 23 | 3297751 | 3434122 | 11036638 | 3.2138 | 3.5
2 | Feb' 23 | 3135440 | 3475513 | 6582908 | 1.8941 | 2.2
3 | Mar' 23 | 3222984 | 3448694 | 11105053 | 3.2201 | 2.21
|  |  | 10358329 | 28724599 | 2.7731 | 3.2243

## 11B
Q-4(Jan-Mar-23)
Year: 2022-23
SoP 011 – B System Average Interruption Duration Index (SAIDI)
Sr. No | Month | ri = Restoration Time for each interruption event | Ni - no of interrupted customers for each sustained interruption event | ri * Ni – Total customer interruption Duration | ri=Restoration Time for each interruption event | Ni= No of Interrupted customers for each sustained Interruption | NT - Total no of customers served | Customer Interruption Duration |  |  | Past year corrosponding Months
[9 empty] | MINS. | HRS.
1 | 2 | 3 | 4 | 5= 3 X 4 | 3 | 4 | 5 | 6 | 7=4/3 | 7A | MINS. | HRS.
1 | Jan' 23 | July |  |  | 688875 | 3297751 | 3434122 | 932011757 | 271.3974 | 0.18819 | 279 | 0.19375
2 | Feb' 23 | August |  |  | 466309 | 3135440 | 3475513 | 619450728 | 178.2329 | 0.12361 | 229 | 0.15903
3 | Mar' 23 |  |  |  | 503700 | 3222984 | 3448694 | 584841739 | 169.5835 | 0.11806 | 167 | 0.11597
[6 empty] | 9656175 | 10358329 | 2136304224 | 206.2402 | 3:43 | 225 | 0.15625

## 11C
Q-4(Jan-Mar-23)
Year: 2022-23
SoP 011 – C: Momentary Average Interruption Frequency Index (MAIFI)
Sr. No | Month | Number of Momentary interruptions Imi | Nmi - Total no of customers for each momentary interruptions | NT - Total no of customers served |  |  | Past year corrosponding Month
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | Jan' 23 | 20071 | 3151427 | 3434122 | 35596422 | 10.3655 | 10.8
2 | Feb' 23 | 14790 | 2827464 | 3475513 | 23090322 | 6.6437 | 6.64
3 | Mar' 23 | 24550 | 3041580 | 3448694 | 38926747 | 11.2874 | 8.73
|  |  |  | 10358329 | 97613491 | 9.4237 | 10.03

## MG SoP - 13
Name of Distribution Licensee: M G V C L
Financial Year: 2022-23
Quarter : Q-IV (Jan-Feb-Mar-2023)
Performa SoP 013: Faulty Meters Replacement
Consumer Category | No. of faulty meters at the start of the quarter | No. of faulty meters added during the quarter | Total no. of defective / faulty Meter | No. of faulty Meters repaired and replaced | No of faulty meters pending at the end of the quarter | Remark
| 1 | 2 | (3)=(2)+(1) | 4 | (5)=(3)-(4)
1 PHASE
MGVCL | 5417 | 23765 | 29182 | 22525 | 6657
3 PHASE
MGVCL | 942 | 2448 | 3390 | 2679 | 711

## SoP_15
Performa SoP 015: Release of New Connection status for FY 2022-23
Qtr | Consumer category | Total no. of consumers connected at the beginning of half-year/year | Pending at the Beginning of the of the Half year/year | New Applications received during the half-year / year | No. of connections released during the half-year / year | No. of applications pending at the end of half-year / year | Total no. of consumers connected at the end of half-year/year
2nd Half (Oct-March23)) | Domestic | 2818959 | 1122 | 34064 | 26368 | 1304 | 2845327
| Commercial (NRGP_C+LTMD_C) | 324529 | 233 | 7606 | 7337 | 304 | 331866
| Industrial LT (NRGP_L+LTMD_L) | 39782 | 15 | 909 | 820 | 164 | 40602
| Agriculture (Total) | 187315 | 8775 | 6376 | 3616 | 8099 | 190931
| Industrial HT | 2822 | 26 | 136 | 86 | 64 | 2869
| Total | 3373407 | 10171 | 49091 | 38227 | 9935 | 3411595

## MG SoP 16
Name of Distribution Licensee: M G V C L
Quarter : Q-4 (Jan-Feb-March- 2023)
Year: 2022-23
Performa SoP 016: Compensation details
COMPENSATION DETAILS
Sr.No. | Event | Compensation | No of cases where compensation was given (in numbers) | Amt of compensation paid (in Rs.)
1 | Duty to provide supply | Rs. 50 per day of delay from the limit specified in the performance regulations | 0 | 0
| a) New Connection |  | 0 | 0
| b) Additional Load |  | 0 | 0
| c) Temporary supply |  | 0 | 0
| d) Shifting service connection |  | 0 | 0
| e)Transfer of service connection |  | 0 | 0
| f) Change in tariff category of consumer |  | 0 | 0
2 | Complaints in billing | Rs. 50 for non reply within the period prescribed in Regulations | 0 | 0
3 | Replacement of meters | LT- Rs. 25 per day of delay - maximum Rs.2,500 and HT - Rs. 250 per day of delay - maximum of Rs.5,000 | 0 | 0
4 | Interruption of supply | LT- Rs. 25 for every 6 hrs of delay- maximum of Rs. 500 and HT- Rs. 50 for every 6 hrs delay- maximum Rs. 1000/- | 0 | 0
5 | Voltage fluctuations and complaints | Rs. 50 for failure to visit or convey findings within the stipulated period | 0 | 0
6 | Responding to consumer's complaints | Rs. 25 for each day of delay- maximum Rs. 500 | 0 | 0
7 | Grievance Handling | Rs.25 for failure in handling grievance | 0 | 0
TOTAL |  |  | 0 | 0